## Annex 2 – Bid Form completed signed and stamped

- All bids must be typed; handwritten bids will not be considered.

- The contract will be awarded to the lowest-cost technically compliant complete lot or complete bid.

- The quantities mentioned below are required unless there is a variation within a specified range with proper justification. The LRC reserves the right to increase or decrease the quantities.

- The bidder is not permitted to alter the section labelled “LRC to complete” below. Bidder is not allowed to use any other template.

- In the event of any discrepancy between the unit price and the total price, LRC reserves the right to rely on the unit price as stated in the financial bid, rather than the total price without go back to the supplier. The unit price must be provided with no more than two decimal places.

- Only one option is allowed for biding

- The bidder shall price each of the three distribution-line schedules separately. All unit rates shall include labor, materials, equipment, transport, testing, permits, overheads, incidental works, and all obligations necessary for the complete execution and handover of the works.

LOT 1:  Site Cleaning, Mobilization & Basement Desludging (B1-B4)

| LRC To Complete |  |  | Bidder To Complete |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Item number | Item/Milestone Required | Required UOM | Estimated Qty | Unit Price in USD, Exclusive VAT | VAT (%) | Unit Price in USD, inclusive VAT | Total Price in USD, inclusive VAT |
| 1.1 | Mobilization & Site Establishment | L.S. | 1 |  |  |  |  |
| 1.2 | General Cleaning - All Floors (incl. Basements) | L.S. | 1 |  |  |  |  |
| 1.3 | Disinfection & Sanitization - All Occupied Spaces | L.S. | 1 |  |  |  |  |
| 1.4 | Dewatering of Basement Levels B3 & B4 | L.S. | 1 |  |  |  |  |
| 1.5 | Cleaning, Disinfection & Sanitization of Flooded Basement Areas (B4 full + B3 40%) | m2 | 3,080 |  |  |  |  |
| 1.6 | Waste, Sludge & Debris Disposal | L.S. | 1 |  |  |  |  |
| 1.7 | Parking-Level Drain & Channel Clearing (All Basement Levels) | L.S. | 1 |  |  |  |  |
| 1.8 | Protection of School Furniture & Equipment | L.S. | 1 |  |  |  |  |
| 1.9 | Post-Vacancy Condition Survey - Whole School (incl. Basement Levels) | L.S. | 1 |  |  |  |  |

LOT 2:  Architectural & Civil Works

| LRC To Complete |  | Bidder To Complete |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Item number | Item/Milestone Required | Required UOM | Estimated Qty | Unit Price in USD, Exclusive VAT | VAT (%) | Unit Price in USD, inclusive VAT | Total Price in USD, inclusive VAT |
| 2.1 | Patch Exterior Wall Openings (Former A/C Sleeves) - Both Faces | No. | 20 |  |  |  |  |
| 2.2 | Localized Wall Plaster & Paint Repair (Moisture Damage) | m2 | 950 |  |  |  |  |
| 2.3 | Crack Repair Below Classroom Windows | No. | 35 |  |  |  |  |
| 2.4 | Refinish Existing Powder-Coated Steel Door Frames | No. | 300 |  |  |  |  |
| 2.5 | Replace Severely Corroded Steel Door Frames | No. | 16 |  |  |  |  |
| 2.6 | Treat/Replace Emergency Push-Bar Hardware | No. | 20 |  |  |  |  |
| 2.7 | Repair/Replace Damaged Door Metal Fittings | No. | 60 |  |  |  |  |
| 2.8 | Repair Door Leaves & Hardware (Wood, Handles) - Classrooms, Toilets & Offices Only | No. | 43 |  |  |  |  |
| 2.9 | Reinstate Missing Wall-Mounted Stair Handrails | m | 110 |  |  |  |  |
| 2.10 | Rehabilitate & Maintain Wall-Mounted Steel Handrail (Existing) | m | 350 |  |  |  |  |
| 2.11 | Rehabilitate & Maintain Above-Parapet Steel Handrail (Existing) | m | 350 |  |  |  |  |
| 2.12 | Grind, Polish & Clean Marble Stair Treads | m | 140 |  |  |  |  |
| 2.13 | Replace Missing Bathroom Mirrors | No. | 35 |  |  |  |  |
| 2.14 | Clean, Secure & Reinstall Suspended Ceiling Strips | m2 | 200 |  |  |  |  |
| 2.15 | Localized Ceiling Repaint | m2 | 180 |  |  |  |  |
| 2.16 | Wall & Ceiling Paint - Super Rubber Paint (Old Walls/Ceilings) | m2 | 9800 |  |  |  |  |
| 2.17 | Wall & Ceiling Paint - Oil Paint (Old Walls/Ceilings) | m2 | 5600 |  |  |  |  |
| 2.18 | Treat & Clean Fairfaced Concrete Ceiling and Walls | m2 | 1400 |  |  |  |  |
| 2.19 | Outside Walls Paint (Existing Walls and Ceilings) | m2 | 3500 |  |  |  |  |
| 2.20 | Paint Damp-Proof Colourless Layer (Unleaded) on Facades | m2 | 3500 |  |  |  |  |
| 2.21 | Replace Guard-Room Exterior Door | No. | 1 |  |  |  |  |
| 2.22 | Replace Guard-Room Toilet Door | No. | 1 |  |  |  |  |
| 2.23 | Replace Guard-Room Kitchen Counter | m | 2 |  |  |  |  |
| 2.24 | Clean & Re-point Sanitary Area Tiling | m2 | 500 |  |  |  |  |
| 2.25 | New Curbstone | m | 15 |  |  |  |  |
| 2.26 | Rehabilitate Existing Curbstone | m | 200 |  |  |  |  |
| 2.27 | Rehabilitate Precast Concrete Tiles (Covered Playgrounds) | m2 | 15 |  |  |  |  |
| 2.28 | New Timber Door (Single Leaf) | No. | 3 |  |  |  |  |
| 2.29 | New Timber Door with View Frame | No. | 8 |  |  |  |  |
| 2.30 | New Steel Double-Leaf Door | No. | 1 |  |  |  |  |
| 2.31 | Repair of Existing Aluminum Windows & Replace Broken Glass | L.S. | 10 |  |  |  |  |
| 2.32 | Tiling Works - Classroom & Corridor Ceramic (60x60cm) | m2 | 85 |  |  |  |  |
| 2.33 | Tiling Works - Kitchen & Toilet Ceramic (30x60 or 30x30cm) | m2 | 5 |  |  |  |  |
| 2.34 | Tiling Works - Laboratory Ceramic (60x60cm, Anti-Acid) | m2 | 5 |  |  |  |  |
| 2.35 | Tiling Works - Skirting | m | 5 |  |  |  |  |
| 2.36 | Repair Existing Broken Floor Tiles & Skirting (All Types) | L.S. | 1 |  |  |  |  |
| 2.37 | Colored P.V.C. Flooring for KG Classrooms | L.S. | 1 |  |  |  |  |
| 2.38 | Handicapped Bathroom Accessories - Vertical Grab Rail | No. | 2 |  |  |  |  |
| 2.39 | Handicapped Bathroom Accessories - Horizontal Grab Rail | No. | 2 |  |  |  |  |
| 2.40 | Handicapped Bathroom Accessories - Drop-Down Removable Arm Rail | No. | 2 |  |  |  |  |
| 2.41 | Handicapped Bathroom Accessories - Emergency Alarm Pull Cord | No. | 2 |  |  |  |  |
| 2.42 | Epoxy Floor - Concrete Benches (Different Colours) | m | 36 |  |  |  |  |
| 2.43 | Signage | No. | 240 |  |  |  |  |

LOT 3:  Mechanical Works

| LRC TO COMPLETE |  |  |  | BIDDERS TO COMPLETE |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Item number | Item/Milestone Required | Required UOM | Estimated Qty | Unit Price in USD, Exclusive VAT | VAT (%) | Unit Price in USD, inclusive VAT | Total Price in USD, inclusive VAT |
| 3.1 | General Technical Requirements & Shop Drawings | Item | 1 |  |  |  |  |
| 3.2 | LAV for Non-Kids - Taps, P-Traps & Angle Valves | No. | 96 |  |  |  |  |
| 3.3 | WC for Non-Kids - Seat Covers, Flushing Hoses & Tank Accessories | No. | 84 |  |  |  |  |
| 3.4 | Water Tank Leak Treatment | No. | 2 |  |  |  |  |
| 3.5 | Float Valves | No. | 10 |  |  |  |  |
| 3.6 | Roof Drains | No. | 9 |  |  |  |  |
| 3.7 | Vertical Pipes Fixation at Top of Roof Level | No. | 10 |  |  |  |  |
| 3.8 | Water Pipe Connection at Roof Level | No. | 1 |  |  |  |  |
| 3.9 | Flushing & Leak Test - Drainage and Water Pipes | item | 1 |  |  |  |  |
| 3.10 | Flushing & Gravity Test - Manholes | item | 1 |  |  |  |  |
| 3.11 | Leak Treatment - Main Drainage Networks (B1/L1 High Level) | item | 1 |  |  |  |  |
| 3.12 | Floor Drain Covers | No. | 60 |  |  |  |  |
| 3.13 | Trench Drain + Rust Treatment/Paint | No. | 1 |  |  |  |  |
| 3.14 | Parking Drain + Rust Treatment/Paint | No. | 20 |  |  |  |  |
| 3.15 | Testing - Drainage Connection to Municipality | item | 1 |  |  |  |  |
| 3.16 | Testing - Water Connection to Municipality | item | 1 |  |  |  |  |
| 3.17 | Parking & Mechanical Rooms - Pipes | Ls | 1 |  |  |  |  |
| 3.18 | Parking & Mechanical Rooms - Ducts | Ls | 1 |  |  |  |  |
| 3.19 | Parking & Mechanical Rooms - Grilles/Registers | Ls | 1 |  |  |  |  |
| 3.20 | Parking & Mechanical Rooms - Sprinklers | Ls | 1 |  |  |  |  |
| 3.21 | Parking Exhaust Fans - Mechanical Rehabilitation & Testing | No. | 4 |  |  |  |  |
| 3.22 | Transfer Booster Pump (B4) - Mechanical Rehabilitation & Testing | No. | 1 |  |  |  |  |
| 3.23 | Submersible Pumps + Sump Pits - Mechanical Rehabilitation & Testing | Set | 2 |  |  |  |  |
| 3.24 | Transfer Booster Pumps (B1) - Mechanical Rehabilitation & Testing | No. | 3 |  |  |  |  |
| 3.25 | Generator Rooms - Ventilation System (Mechanical) | No. | 3 |  |  |  |  |
| 3.26 | Generator Rooms - Sound Insulation | Ls | 1 |  |  |  |  |
| 3.27 | Generator Rooms - Pipes Insulation | Ls | 1 |  |  |  |  |
| 3.28 | Generator Rooms - Fuel Oil Piping & Connections | Ls | 1 |  |  |  |  |
| 3.29 | Generator Rooms - Fill Cabinet | No. | 1 |  |  |  |  |
| 3.30 | Generator Rooms - Oil Filter Replacement | No. | 3 |  |  |  |  |
| 3.31 | Exhaust Fans - Mechanical Rehabilitation & Testing | No. | 41 |  |  |  |  |
| 3.32 | Replace Broken Kids WC (K.G.) | No. | 6 |  |  |  |  |
| 3.33 | Replace Broken Non-Kids WC | No. | 5 |  |  |  |  |
| 3.34 | Replace Broken Kids Lavatories (K.G.) | No. | 6 |  |  |  |  |
| 3.35 | Replace Broken Non-Kids Lavatories | No. | 5 |  |  |  |  |
| 3.36 | Self-Close Taps - Kids & Students Lavatories | No. | 14 |  |  |  |  |
| 3.37 | Self-Close Taps - Drinking Basins | No. | 12 |  |  |  |  |
| 3.38 | Kitchen Sink Accessories | No. | 3 |  |  |  |  |
| 3.39 | Shower Head & Mixer Replacement | No. | 2 |  |  |  |  |
| 3.40 | Janitor Sink & Bathroom Accessories (JS) | No. | 8 |  |  |  |  |
| 3.41 | Repair Option (Alt. 1) - Reinstate Relocated Drinking Fountains | No. | 40 |  |  |  |  |
| 3.42 | Repair Option (Alt. 2) - Supply New Drinking Fountains (Missing/Damaged) | No. | 16 |  |  |  |  |
| 3.43 | Rainwater Collection Tanks - Playground | No. | 8 |  |  |  |  |
| 3.44 | Electric Water Heater Replacement | No. | 1 |  |  |  |  |
| 3.45 | Ramp-Top Stormwater Interception Drain (B3 & B4 Entry Ramps) | m | 14 |  |  |  |  |
| 3.46 | Flood Barriers, Backflow Valves & Sealing (B3 & B4 Entries + Drainage) | L.S. | 1 |  |  |  |  |
| 3.47 | Potable Water Treatment Station - Rehabilitation | No. | 1 |  |  |  |  |
| 3.48 | Alternate Alt 3 - Remove All Drinking Fountains & Make Good Walls (In Lieu of Repair Option Items Above) | No. | 56 |  |  |  |  |

LOT 4:  Electrical Works

| LRC TO COMPLETE |  |  |  | BIDDERS TO COMPLETE |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Item number | Item/Milestone Required | Required UOM | Estimated Qty | Unit Price in USD, Exclusive VAT | VAT (%) | Unit Price in USD, inclusive VAT | Total Price in USD, inclusive VAT |
| 4.1 | Solar Inverter Room - Access & Inspection | L.S. | 1 |  |  |  |  |
| 4.2 | Remove Temporary Cabling & Reinstate Proper Connection | L.S. | 1 |  |  |  |  |
| 4.3 | Fixing and Repairing - General Cables, Wires, Panels | L.S. | 1 |  |  |  |  |
| 4.4 | Disconnecting Switches - 4x63A 4-Pole Waterproof (Basement) | No. | 2 |  |  |  |  |
| 4.5 | Disconnecting Switches - 4x40A 4-Pole Waterproof (Basement) | No. | 6 |  |  |  |  |
| 4.6 | Electrical Sockets - 16A Simplex 2P+E | No. | 40 |  |  |  |  |
| 4.7 | Electrical Sockets - 16A Simplex Waterproof | No. | 20 |  |  |  |  |
| 4.8 | Electrical Sockets - 16A Simplex UPS Socket | No. | 10 |  |  |  |  |
| 4.9 | Switches - 10A One Way One Gang | No. | 16 |  |  |  |  |
| 4.10 | Switches - 10A One Way Two Gangs | No. | 16 |  |  |  |  |
| 4.11 | Switches - 10A Two Ways One Gang | No. | 6 |  |  |  |  |
| 4.12 | Switches - 10A Two Ways Two Gangs | No. | 6 |  |  |  |  |
| 4.13 | Staircase Light Push-Button (Minuterie) | No. | 20 |  |  |  |  |
| 4.14 | Lighting Fixtures - TYPE B Twin T8 LED (Replace Complete) | No. | 100 |  |  |  |  |
| 4.15 | Lighting Fixtures - TYPE B Tube Replacement Only | No. | 200 |  |  |  |  |
| 4.16 | Lighting Fixtures - TYPE A 120cm LED Panel (Classroom) | No. | 50 |  |  |  |  |
| 4.17 | Lighting Fixtures - TYPE A1 LED Panel (Corridor) | No. | 50 |  |  |  |  |
| 4.18 | Lighting Fixtures - TYPE H Round Spot (Ground Floor) | No. | 8 |  |  |  |  |
| 4.19 | Lighting Fixtures - E27 LED 14W | No. | 50 |  |  |  |  |
| 4.20 | Lighting Fixtures - TYPE CC Twin T8 LED (WC) | No. | 10 |  |  |  |  |
| 4.21 | Lighting Fixtures - TYPE M Motion-Sensor LED | No. | 10 |  |  |  |  |
| 4.22 | Lighting Fixtures - Emergency (Replace Existing EM) | No. | 50 |  |  |  |  |
| 4.23 | Lighting Fixtures - Exit Signs (Replace Existing) | No. | 10 |  |  |  |  |
| 4.24 | Test UPS System (No Replacement) | L.S. | 1 |  |  |  |  |
| 4.25 | Replace Damaged Photovoltaic Panels (600W) | No. | 15 |  |  |  |  |
| 4.26 | Rooftop Access / Working-at-Height Provision | L.S. | 1 |  |  |  |  |
| 4.27 | Parking Management System - Test Only (No Repair) | L.S. | 1 |  |  |  |  |
| 4.28 | Replace Damaged Cabling - Lighting & Power Circuits, Flooded Basement Levels (B3 40% + B4 100%) | m2 | 3080 |  |  |  |  |
| 4.29 | Replace Feeder Cables to Pumps & Panels - Flooded Basement Levels | L.S. | 1 |  |  |  |  |
| 4.30 | Electrical Reconnection & Testing - Mechanical Equipment | L.S. | 1 |  |  |  |  |
| 4.31 | Earthing System - Testing | L.S. | 1 |  |  |  |  |
| 4.32 | Lightning Protection System | L.S. | 1 |  |  |  |  |
| 4.33 | Hybrid Inverter system upgrade | L.S. | 1 |  |  |  |  |
| 4.34 | Distribution Boards - Testing & Certification | L.S. | 1 |  |  |  |  |
| 4.35 | Final Testing & Handover Certification | L.S. | 1 |  |  |  |  |

| Divisions | Items by Trade | Total Exc (VAT) | Total (Inc VAT) |
| --- | --- | --- | --- |
| Division 1 | Site Cleaning, Mobilization & Basement Desludging (B1-B4) |  |  |
| Division 2 | Architectural & Civil Works |  |  |
| Division 3 | Mechanical Works |  |  |
| Division 4 | Electrical Works |  |  |
| Grand Total |  |  |  |

## ANNEX 3: DETAILED SPECIFICATIONS

As per: 2026-092 Terms of Reference

| LRC To Complete |  |  |
| --- | --- | --- |
| Item number | Item/Milestone Required | Detailed Specifications and Requirements |
| 1.1 | Mobilization & Site Establishment | Mobilize personnel, equipment, temporary site facilities, signage and safety barriers, and set up welfare and storage facilities for the duration of the works. Work to include: coordination of site access and working hours with the school administration and LRC Engineer; submission of a method statement and programme prior to start of works; and all labour, equipment and materials needed to establish the site, to the satisfaction of the Engineer. |
| 1.2 | General Cleaning - All Floors (incl. Basements) | Thorough cleaning of the school premises, including collection, removal, loading, transportation and lawful disposal of accumulated litter, waste, debris and unwanted materials from classrooms, corridors, staircases, offices, laboratories, WCs, playgrounds, external areas, roofs, sun-shading canopies, terraces and balconies (per the original specification), extended to also cover basement levels B1 and B2 (unaffected by flooding; B3 and B4 are covered separately under Item 1.5 given the heavier flood/sewage-remediation scope there). Work to include: sweeping and gathering of all affected areas, with particular thoroughness at corridors, staircases and balconies; removal of loose fixtures/rubbish left by prior occupants; wet-wiping of accessible surfaces; and leaving the premises clean, safe and ready for use, to the satisfaction of the Engineer. |
| 1.3 | Disinfection & Sanitization - All Occupied Spaces | Supply and apply approved disinfectant/sanitizing agents to all classrooms, rooms, offices, laboratories, WCs, corridors, terraces and balconies throughout the building (basement levels B1 and B2, and Ground Floor to Floor 6 — B3 and B4 are covered separately under Item 1.5), given the building's recent use as a displacement shelter. Work to include: all disinfectant materials, application equipment and labour; surface disinfection of floors, walls (to hand height), door handles, sanitary fixtures and fittings; and appropriate PPE and ventilation during application, all to the satisfaction of the Engineer. |
| 1.4 | Dewatering of Basement Levels B3 & B4 | Supply, install and operate pumps and dewatering equipment as required to remove standing water from basement level B4 (fully flooded) and the flooded portion of basement level B3 (40% of floor area). Work to include: all pumping equipment, hoses and power supply; safe discharge of pumped water to an approved point; and continuation of pumping until the affected areas are free of standing water, to the satisfaction of the Engineer. |
| 1.5 | Cleaning, Disinfection & Sanitization of Flooded Basement Areas (B4 full + B3 40%) | Comprehensive cleaning, disinfection and sanitization of basement level B4 (fully flooded, 2,200 m²) and the flooded portion of basement level B3 (40% of 2,200 m² = 880 m²) following exposure to rainwater/sewage flooding and accumulated waste, particularly around staircases. Work to include: removal of sludge, contaminated residues and floating debris; washing of all affected floor and wall surfaces; application of approved disinfectant; and implementation of appropriate health, safety and hygiene measures (PPE, ventilation, controlled access) given the nature of the contamination. Basement levels B1 and B2 (unaffected by flooding) are covered under the general cleaning and disinfection items above. |
| 1.6 | Waste, Sludge & Debris Disposal | Collection, transportation and disposal of all waste, sludge and debris generated by the cleaning works, to approved dumps, during a time agreed between the school administration, Contractor and LRC Engineer. Work to include: all handling, loading and transport equipment; segregation of contaminated waste where required by the receiving facility; and all disposal/tipping fees, at the Contractor's cost and responsibility and in an environmentally sound manner. LRC shall bear no responsibility for handling, transport or final disposal. |
| 1.7 | Parking-Level Drain & Channel Clearing (All Basement Levels) | Clear accumulated debris from parking-area floor drains, trench drains and drainage channels across all four basement levels ahead of the mechanical rehabilitation works. Work to include: manual/mechanical removal of silt and debris from drain bodies and channels; confirmation that drains run free; and lawful disposal of removed material, to the satisfaction of the Engineer. |
| 1.8 | Protection of School Furniture & Equipment | The Contractor is fully responsible, and at his own cost, to relocate the school's furniture, appliances, documents, cameras, computers, etc. during the works and where needed. The Contractor is fully responsible to protect the school's furniture, appliances, documents, cameras, computers, etc. from any damage during the whole period of the works, and shall repair or purchase at his own cost new furniture, appliances, documents, cameras, computers, etc. if damaged by his labour and works. |
| 1.9 | Post-Vacancy Condition Survey - Whole School (incl. Basement Levels) | Following full vacancy of the school and completion of the cleaning and disinfection works, carry out and submit a detailed condition survey covering the ENTIRE building, not only the basement levels. Particular attention to be given to: (a) basement levels B3 and B4, to define the scope of any further finishes-repair works there; and (b) any classrooms, offices, stores or other rooms throughout the school that were previously occupied by displaced persons, kept locked, or otherwise inaccessible during the initial assessment, to identify any additional defects not visible at that time. Work to include: a room-by-room photographic record across all floors; a written assessment of floor, wall, door and MEP component condition; and a summary report identifying items requiring repair, submitted to the LRC Engineer for approval before any further works in the affected areas are instructed. |

| Item number | Item/Milestone Required | Detailed Specifications and Requirements |
| --- | --- | --- |
| 2.1 | Patch Exterior Wall Openings (Former A/C Sleeves) - Both Faces | Cut back, fill and make good 20 no. openings (10 cm radius) left in the exterior walls from temporary air-conditioning unit installations, accessed and finished from BOTH the interior and exterior faces. Work to include: cutting back and cleaning the opening; cement mortar fill; render reinstatement to match existing texture; paint finish matching existing colour on both sides; and any scaffolding, ladders or rope access equipment required for exterior work above ground level, to the satisfaction of the Engineer. |
| 2.2 | Localized Wall Plaster & Paint Repair (Moisture Damage) | Rehabilitate and repair cracked and damaged plaster in indoor and outdoor areas. Work to include: determine the location and remove all loose material around the area; remove the cracked plaster layer; install galvanized steel mesh (20 cm width minimum); clean the affected areas with suitable materials; reinstate plaster and apply paint finish to match existing colour and texture. Priority to lower wall sections above skirting and former drinking-fountain locations, where deterioration is linked to moisture/water presence, all as per specifications and Engineer's instructions. |
| 2.3 | Crack Repair Below Classroom Windows | Rehabilitate and repair cracks observed below windows in classrooms. Work to include: routing out and cleaning of the crack; filling with suitable crack-repair compound; reinstatement of plaster; and repainting of the affected area to match existing colour and finish, all to the satisfaction of the Engineer. |
| 2.4 | Refinish Existing Powder-Coated Steel Door Frames | Refinish existing powder-coated steel door frames to restore an as-new appearance, representing the majority of frames assessed to be in serviceable condition. Work to include: on-site surface preparation (sanding/etching/degreasing); application of a 2-pack enamel or equivalent system compatible with the existing powder-coat finish; and colour-matching to existing. Full factory re-powder-coating is not required. |
| 2.5 | Replace Severely Corroded Steel Door Frames | Supply and install new steel door frames matching existing size, type and finish, at locations where the existing frame is found to be severely corroded beyond repair, particularly in toilet areas. Work to include: removal and disposal of the existing frame; making good the surrounding wall/reveal finish; supply and fixing of the new frame with all related accessories; and finishing paint, all as per specifications. |
| 2.6 | Treat/Replace Emergency Push-Bar Hardware | Clean and apply anti-rust treatment to emergency/panic push-bar hardware on stair doors showing light surface rust, and confirm smooth operation. Work to include: full replacement of the push-bar unit, with all fixings, at locations where treatment alone is not sufficient to restore safe operation. |
| 2.7 | Repair/Replace Damaged Door Metal Fittings | Repair or replace missing or damaged door metal fittings and accessories (hinges, closers, handles, locksets) at various locations throughout the building. Work to include: removal of damaged fittings; supply and fixing of new fittings of similar type and quality to existing; and adjustment to confirm smooth, safe operation of the door. |
| 2.8 | Repair Door Leaves & Hardware (Wood, Handles) - Classrooms, Toilets & Offices Only | Repair damaged door leaves and hardware limited to classrooms, toilets/WCs and administrative offices only - corridors, staircases, labs, storerooms and mechanical/electrical rooms are excluded from this item. Work to include: repair of delaminated/water-damaged panels, edges and cores; replacement of damaged handles, hinges and locks; and re-hanging/adjustment for smooth operation, finished to match existing. Priority to toilet/WC cubicle and entry doors, followed by classroom and office doors, per the condition assessment findings. |
| 2.9 | Reinstate Missing Wall-Mounted Stair Handrails | Supply and install new steel wall-mounted handrail at stairs, similar to existing in shape, form, length, finish and colour, at locations currently missing a handrail. Item to include labour, equipment, material and all works required to complete the works. Contractor to submit shop drawings and samples prior to installation, for the Engineer's approval. |
| 2.10 | Rehabilitate & Maintain Wall-Mounted Steel Handrail (Existing) | Rehabilitate and maintain existing wall-mounted steel handrails at staircases and balconies, returning them to their original form and condition. Work to include: straightening and welding of loose, bent or detached sections; grinding and polishing of welded joints; anti-rust treatment; and repainting to match existing colour and finish, all as per specifications and to the Engineer's approval. |
| 2.11 | Rehabilitate & Maintain Above-Parapet Steel Handrail (Existing) | Rehabilitate and maintain existing above-parapet steel handrails, returning them to their original form and condition. Work to include: straightening and welding of loose, bent or detached sections; grinding and polishing of welded joints; anti-rust treatment; and repainting to match existing colour and finish, all as per specifications and to the Engineer's approval. |
| 2.12 | Grind, Polish & Clean Marble Stair Treads | Grind, polish and clean existing marble stair treads showing general wear, to restore a smooth, non-slip and presentable surface. Work to include: diamond grinding of the tread surface, polishing to a consistent finish matching adjacent treads, and final cleaning, all to the satisfaction of the Engineer. |
| 2.13 | Replace Missing Bathroom Mirrors | Supply and install new mirrors at bathroom/lavatory locations found missing. Work to include: mirror glass with polished edges, dimensions as per site conditions; anti-corrosion wall-fixing hardware suitable for a humid environment; and sealing of edges,similar to the existing and according to the Engineer's approval. |
| 2.14 | Clean, Secure & Reinstall Suspended Ceiling Strips | Supply and install aluminum strip suspended ceiling as per specifications, and fix or replace any damaged part. Work to include: materials (aluminum sheet thickness similar to existing); labour; accessories; angles; and a heavy-duty metal suspension system, cleaned and secured throughout, similar to existing. |
| 2.15 | Localized Ceiling Repaint | Rehabilitate and repaint ceiling areas including corridor soffits and stairwell void edges. Work to include: surface preparation (cleaning, filling of minor imperfections); application of primer where bare substrate is exposed; and two coats of finish paint matching existing colour, to the satisfaction of the Engineer. |
| 2.16 | Wall & Ceiling Paint - Super Rubber Paint (Old Walls/Ceilings) | Supply and apply super rubber paint to old internal walls and ceilings. Work to include: surface preparation, filling of minor imperfections, primer where bare substrate is exposed, and two coats of finish paint, colour as directed by the Engineer. Quantity is 70% of the original design's building-wide allowance (14,000 m²), per LRC's phased-scope decision. |
| 2.17 | Wall & Ceiling Paint - Oil Paint (Old Walls/Ceilings) | Supply and apply oil paint to old internal walls and ceilings. Work to include: surface preparation, primer where required, and two coats of finish paint, colour as directed by the Engineer. Quantity is 70% of the original design's building-wide allowance (8,000 m²), per LRC's phased-scope decision. |
| 2.18 | Treat & Clean Fairfaced Concrete Ceiling and Walls | Treat and clean existing fairfaced (exposed) concrete ceiling and wall surfaces. Work to include: cleaning of surface contamination, minor patch repair, and application of an approved clear protective/sealing treatment to restore appearance. Quantity is 70% of the original design's building-wide allowance (2,000 m²), per LRC's phased-scope decision. |
| 2.19 | Outside Walls Paint (Existing Walls and Ceilings) | Paint for external old and new walls, smooth touch. Work to include: removal of any loose paint or obstacles; rehabilitation of the surface and making it good; polyurethane sealant where needed for cracks; and application of 2 coats of exterior-grade paint. Quantity is 70% of the original design's building-wide allowance (5,000 m²), per LRC's phased-scope decision. |
| 2.20 | Paint Damp-Proof Colourless Layer (Unleaded) on Facades | Supply and paint with damp-proof paint after cleaning and washing all walls; remove the existing paint and enlarge all cracks, especially at the intersection of hollow concrete blocks and reinforced concrete elements, prior to application. Quantity is 70% of the original design's building-wide allowance (5,000 m²), per LRC's phased-scope decision. |
| 2.21 | Replace Guard-Room Exterior Door | Supply and install new external door for the guard room, found in poor condition, suitable for the security/access requirements of the location. Work to include: new door leaf and frame, all hardware (hinges, lockset, handle), and finishing paint to both faces of the door and box frame, similar to existing in size and function. |
| 2.22 | Replace Guard-Room Toilet Door | Supply and install new solid single-leaf flush timber door similar to existing, with a minimum 10 cm wide frame between the plywood faces filled with timber beads (tongue and groove, each 5 cm), and door edges in bead wood fixed by tongue and groove frames, all as specified. Work to include all accessories and fittings (hinges, lockset, handle), and finishing paint to both faces of the door leaf and the box frame. |
| 2.23 | Replace Guard-Room Kitchen Counter | Supply and install new marble worktop (counter) for the guard room's kitchenette, similar to existing in size, thickness and finish, to replace the damaged unit. Work to include: removal and disposal of the existing counter, supply and fixing of the new marble top with polished edges, and sealing to the adjoining cabinetry. |
| 2.24 | Clean & Re-point Sanitary Area Tiling | General cleaning and re-pointing/grouting of wall and floor tiling and joints in bathroom areas throughout the building. Work to include: removal of degraded/discoloured grout, cleaning of tile surfaces, and reinstatement of grout/pointing matching existing colour, to a sound, hygienic finish. |
| 2.25 | New Curbstone | Supply and install new precast fairfaced concrete curbstone as per specifications. Work to include: labour, material and equipment; curb fill and mortar; removal of existing damaged units; casting of concrete behind the curbstone; and handicapped concrete units where required. All works as per specifications and Engineer's instructions. |
| 2.26 | Rehabilitate Existing Curbstone | Inspect and rehabilitate existing curbstone as per specifications. Work to include: removal of all loose or damaged parts and re-installation as existing; materials; and cleaning. All works as per specifications and Engineer's instructions. |
| 2.27 | Rehabilitate Precast Concrete Tiles (Covered Playgrounds) | Supply and install precast concrete tiles similar to existing. Samples to be provided for approval. Work to include: labour, material and equipment; the necessary fill below tiles; and installation of tiles, all as per specifications and Engineer's instructions. |
| 2.28 | New Timber Door (Single Leaf) | Supply and install flush timber door with laminated plastic facing. The door shall have a 10 cm wide frame between the plywood, filled with timber beads by tongue and groove (each 5 cm), and the door edges shall be bead wood, fixed by tongue and groove frames, all as specified. Work to include all accessories and fittings, pre-painting and finishing paint to both sides of the door and box frame. |
| 2.29 | New Timber Door with View Frame | As Item 2.28 (flush timber door with laminated plastic facing, 10 cm frame, timber bead tongue-and-groove construction, all accessories, fittings and finishing paint), with the addition of a vision/view frame (glazed panel) incorporated into the door leaf, as per specifications. |
| 2.30 | New Steel Double-Leaf Door | Supply and install new steel double-leaf door with related accessories, similar to existing, as per specifications. Work to include: two door leaves, frame, all hardware (hinges, lockset, handle) and finishing paint to both faces of the door leaves and box frame. |
| 2.31 | Repair of Existing Aluminum Windows & Replace Broken Glass | Repair existing aluminum windows and replace broken glass throughout the building. Work to include: checking the functionality of latches, hinges and other hardware, and replacing broken parts with new ones so each window operates smoothly; removal and replacement of cracked/broken glass panes to match existing type and thickness; and application of a high-quality sealant around all edges to prevent moisture ingress, with all associated finishing works. |
| 2.32 | Tiling Works - Classroom & Corridor Ceramic (60x60cm) | Supply and install anti-skid coloured ceramic tiles, 60 x 60 cm, first choice, for classrooms and corridors. Work to include: surface preparation, bedding mortar, tile laying to true line and level, and grouting to match tile colour & similar to the existing. |
| 2.33 | Tiling Works - Kitchen & Toilet Ceramic (30x60 or 30x30cm) | Supply and install anti-skid coloured ceramic tiles, 30 x 60 cm or 30 x 30 cm, for kitchens and toilets. Work to include: surface preparation, bedding mortar, tile laying to true line and level, and grouting to match tile colour& similar to the existing . |
| 2.34 | Tiling Works - Laboratory Ceramic (60x60cm, Anti-Acid) | Supply and install anti-acid and anti-skid coloured ceramic tiles, 60 x 60 cm, for laboratories. Work to include: surface preparation, bedding mortar, tile laying to true line and level, and chemical-resistant grouting& similar to the existing. |
| 2.35 | Tiling Works - Skirting | Supply and install skirting tiles to match flooring finish (10 cm height), same type and matching colour as the ceramic floor tiles, neatly fixed and grouted to the wall/floor junction. |
| 2.36 | Repair Existing Broken Floor Tiles & Skirting (All Types) | Inspect the entire floor area, then rehabilitate and repair all damaged and broken tiles and skirting of any type (marble, ceramic, mosaic, cement). Work to include: removal of all debris as specified; all materials and labour; matching of tile shape, thickness, dimension and pattern to existing; and reinstatement similar to existing, for all rooms and corridors, to the Engineer's approval. |
| 2.37 | Colored P.V.C. Flooring for KG Classrooms | Rehabilitate and clean existing coloured PVC flooring for KG classrooms. Work to include: cutting and patching of damaged areas (matching thickness, shape and colour); welding of joints; fixing of skirting; and general cleaning, with all works approved by the Engineer prior to installation. |
| 2.38 | Handicapped Bathroom Accessories - Vertical Grab Rail | Supply and install vertical grab rail, 60 cm bars, complete with heavy-duty anti-corrosion fixings suitable for a wet environment, to the Engineer's approval. |
| 2.39 | Handicapped Bathroom Accessories - Horizontal Grab Rail | Supply and install horizontal grab rail, 60 cm bars, complete with heavy-duty anti-corrosion fixings suitable for a wet environment, to the Engineer's approval. |
| 2.40 | Handicapped Bathroom Accessories - Drop-Down Removable Arm Rail | Supply and install drop-down rail, removable arm, 80 cm, complete with heavy-duty anti-corrosion fixings suitable for a wet environment, to the Engineer's approval. |
| 2.41 | Handicapped Bathroom Accessories - Emergency Alarm Pull Cord | Supply and install alarm pull cord for emergency use, wired to the nurse/supervisor station, complete with all accessories and testing prior to handover. |
| 2.42 | Epoxy Floor - Concrete Benches (Different Colours) | Supply and install epoxy with polyurethane layer finishing on existing concrete benches, different colours, suitable for playground use. Work to include: surface preparation and cleaning of the existing bench, filling of any cracks or chips, and application of the epoxy/polyurethane finish system to a durable, weather-resistant standard. |
| 2.43 | Signage | Supply and install sliding panel signs for all rooms, high-pressure laminate (HPL) 1.2 cm thick, movable inside a stainless steel rail (316), fixed on walls, letters vinyl-printed with engravement for special-need purposes. Colours and shape as per Engineer's instruction. Dimension: 20cm x 10cm. |

| Item number | Item/Milestone Required | Detailed Specifications and Requirements |
| --- | --- | --- |
| 3.1 | General Technical Requirements & Shop Drawings | Prepare shop drawings for all mechanical works for the Engineer's approval prior to execution, and mobilize for maintenance, rehabilitation, testing and commissioning of the existing mechanical systems. Work to include: survey of existing installations, preparation of drawings/method statements, and submission for approval before any works commence. |
| 3.2 | LAV for Non-Kids - Taps, P-Traps & Angle Valves | Supply and install new taps, P-traps and angle valves with flexible pipe connections for non-kids lavatories throughout the building, similar to existing. Work to include: removal and disposal of the existing failed fittings, supply of new fittings of equivalent or better quality, connection to existing supply and waste points, and testing for leaks. |
| 3.3 | WC for Non-Kids - Seat Covers, Flushing Hoses & Tank Accessories | Supply and install new seat covers, flushing hoses, tank accessories, and angle valves with flexible pipe connections for non-kids WCs throughout the building, similar to existing. Work to include: removal and disposal of failed components, fitting of new components, and testing of flush and shut-off operation. |
| 3.4 | Water Tank Leak Treatment | Treat water leakage from the two existing 10,000-litre PE tanks located at roof level. Work to include: locating the source of leakage, cleaning and preparing the affected surface, application of an approved leak-sealing compound/patch suitable for potable water contact, and confirmation the tank holds water without leaking. |
| 3.5 | Float Valves | Test and rehabilitate float valves at water tanks and cisterns to confirm correct shut-off operation. Work to include: removal of the existing valve where faulty, supply and fitting of a new valve of matching size/type, and testing of water level control. |
| 3.6 | Roof Drains | Clean and rehabilitate roof drains located on the roof. Work to include: removal of debris and blockages, checking and repair of the drain body and strainer, and confirmation of free-flowing drainage. |
| 3.7 | Vertical Pipes Fixation at Top of Roof Level | Reinstall and re-secure vertical water filling pipes at roof level in a proper technical manner. Work to include: supply of new pipe clips/brackets as required, correct alignment and fixing of pipework, and confirmation the installation is stable and watertight. |
| 3.8 | Water Pipe Connection at Roof Level | Reinstate and reconnect water pipe connections at roof level, including a previously disconnected water pipe, as required. Work to include: supply of any missing fittings, jointing/sealing of connections, and pressure/leak testing on completion. |
| 3.9 | Flushing & Leak Test - Drainage and Water Pipes | Carry out flushing and leak testing for the existing drainage and water pipes throughout the building. Work to include: flushing of all accessible lines to clear debris, pressure/gravity testing as applicable, identification of any leaks or blockages, and repair of any defects found to achieve a fully functioning system. |
| 3.10 | Flushing & Gravity Test - Manholes | Carry out flushing and gravity testing for the existing manholes and related pipe connections. Work to include: opening and inspecting manholes, flushing connected pipe runs, confirming correct fall/gravity flow, and repair of any defects found. |
| 3.11 | Leak Treatment - Main Drainage Networks (B1/L1 High Level) | Treat leaks in the main drainage networks at basement B1 / Level 1 high level. Work to include: locating the source of the leak, exposing the pipe/joint as necessary, repair or replacement of the defective section, and confirmation of a leak-free system on completion. |
| 3.12 | Floor Drain Covers | Supply and install new floor drain covers throughout the building, similar to existing, complete with cleaning of the drain body beneath each cover. |
| 3.13 | Trench Drain + Rust Treatment/Paint | Clean and rehabilitate the trench drain at parking level. Work to include: removal of debris and silt, rust treatment of steel grating/frame, and repainting of steel parts to prevent further corrosion. |
| 3.14 | Parking Drain + Rust Treatment/Paint | Clean and rehabilitate parking-level drain outlets. Work to include: removal of debris and silt, rust treatment of steel grating/frame, and repainting of steel parts to prevent further corrosion. |
| 3.15 | Testing - Drainage Connection to Municipality | Test the drainage connection to the municipal network to confirm it is functioning correctly and free of blockages or backflow, and report any deficiencies to the LRC Engineer. |
| 3.16 | Testing - Water Connection to Municipality | Test the water supply connection to the municipal network to confirm adequate pressure and supply, and report any deficiencies to the LRC Engineer. |
| 3.17 | Parking & Mechanical Rooms - Pipes | Carry out maintenance, rehabilitation, testing and commissioning of pipework within the parking and mechanical rooms. Work to include: inspection of all accessible pipe runs, repair or replacement of damaged sections, re-fixing of loose supports, and pressure testing on completion. |
| 3.18 | Parking & Mechanical Rooms - Ducts | Carry out maintenance, rehabilitation, testing and commissioning of ductwork within the parking and mechanical rooms. Work to include: inspection of accessible ductwork, repair of damaged sections and joints, re-fixing of loose supports, and confirmation of correct airflow. |
| 3.19 | Parking & Mechanical Rooms - Grilles/Registers | Carry out maintenance, rehabilitation, testing and commissioning of grilles and registers within the parking and mechanical rooms. Work to include: cleaning, repair or replacement of damaged grilles/registers, and confirmation of free operation of adjustable louvres. |
| 3.20 | Parking & Mechanical Rooms - Sprinklers | Carry out maintenance, rehabilitation, testing and commissioning of the sprinkler system within the parking and mechanical rooms. Work to include: inspection of sprinkler heads and pipework, replacement of damaged/corroded heads, and flow testing to confirm the system is operational. |
| 3.21 | Parking Exhaust Fans - Mechanical Rehabilitation & Testing | Mechanically rehabilitate and test parking-level exhaust fans, repairing identified mechanical faults. Work to include: inspection of fan blades, bearings and mounts; cleaning and lubrication; repair or replacement of faulty mechanical components; and confirmation of free rotation. Electrical connection/reconnection of the fans is covered under the Electrical Works Lot. |
| 3.22 | Transfer Booster Pump (B4) - Mechanical Rehabilitation & Testing | Mechanically rehabilitate and test the transfer booster pump located at B4. Work to include: inspection of pump casing, seals and couplings, repair or replacement of worn mechanical components, and confirmation of correct mechanical operation. Electrical connection is covered under the Electrical Works Lot. |
| 3.23 | Submersible Pumps + Sump Pits - Mechanical Rehabilitation & Testing | Mechanically rehabilitate and test submersible pumps and associated sump pits. Work to include: removal and inspection of each pump, repair or replacement of the pump unit where beyond economical repair, cleaning and repair/replacement of sump pit covers, and confirmation of correct mechanical operation. Electrical connection is covered under the Electrical Works lot. |
| 3.24 | Transfer Booster Pumps (B1) - Mechanical Rehabilitation & Testing | Mechanically rehabilitate and test transfer booster pumps located at B1. Work to include: inspection of pump casings, seals and couplings, repair or replacement of worn mechanical components, and confirmation of correct mechanical operation. Electrical connection is covered under the Electrical Works Lot. |
| 3.25 | Generator Rooms - Ventilation System (Mechanical) | Mechanically check and repair the ventilation system, interlocked with generator operation, for each of the three generator rooms. Work to include: inspection of louvres, dampers and ductwork, repair or replacement of damaged mechanical components, and confirmation of correct airflow when the generator runs. |
| 3.26 | Generator Rooms - Sound Insulation | Check and repair sound insulation within the generator rooms. Work to include: inspection of existing acoustic lining/panels, repair or replacement of damaged sections, and re-fixing to achieve the original level of sound attenuation. |
| 3.27 | Generator Rooms - Pipes Insulation | Repair pipe insulation within the generator rooms. Work to include: removal of damaged/degraded insulation, supply and fitting of new insulation matching existing thickness and type, and finishing with protective cladding where originally provided. |
| 3.28 | Generator Rooms - Fuel Oil Piping & Connections | Inspect and repair fuel oil piping and connections to the generators. Work to include: checking all joints and fittings for leaks, repair or replacement of defective sections, and pressure/leak testing on completion. |
| 3.29 | Generator Rooms - Fill Cabinet | Check and repair the fuel fill cabinet. Work to include: inspection of the cabinet door, seals and fill point fittings, repair or replacement of damaged components, and confirmation of secure, leak-free operation. |
| 3.30 | Generator Rooms - Oil Filter Replacement | Supply and replace oil filters for the three generators, of the correct type and specification for each unit, with disposal of the used filters in an environmentally sound manner. |
| 3.31 | Exhaust Fans - Mechanical Rehabilitation & Testing | Check and rehabilitate existing exhaust fans throughout the building, mechanical scope only. Work to include: all ductwork connections via flexible connections, dampers, attenuators, acoustic cladding to connection ductwork, and inspection doors, identification and bonding, and all sundry mechanical items needed to restore each fan to correct operation. Electrical/control power wiring and reconnection is covered under the Electrical Works Lot. |
| 3.32 | Replace Broken Kids WC (K.G.) | Supply and install new WC (EWC, same sizing as existing) for the kindergarten, complete with all accessories, to replace units found broken. Work to include: removal and disposal of the broken unit, supply and fixing of the new unit, connection to existing supply and waste, and testing of flush operation. |
| 3.33 | Replace Broken Non-Kids WC | Supply and install new WC (EWC, same sizing as existing) for non-kids areas, complete with all accessories, to replace units found broken. Work to include: removal and disposal of the broken unit, supply and fixing of the new unit, connection to existing supply and waste, and testing of flush operation. |
| 3.34 | Replace Broken Kids Lavatories (K.G.) | Supply and install new wall-hung lavatory (45 x 35 cm) for kids in the K.G., complete with all accessories, to replace units found broken. Work to include: removal and disposal of the broken unit, supply and fixing of the new unit, connection to existing supply and waste, and leak testing. |
| 3.35 | Replace Broken Non-Kids Lavatories | Supply and install new semi-pedestal lavatory with mixer (55 x 45 cm) for non-kids areas, complete with all accessories, to replace units found broken. Work to include: removal and disposal of the broken unit, supply and fixing of the new unit, connection to existing supply and waste, and leak testing. |
| 3.36 | Self-Close Taps - Kids & Students Lavatories | Supply and install self-close taps on kids' and students' lavatories, similar to existing. Work to include: removal of the existing tap, fitting of the new self-close mechanism, connection to supply, and testing of shut-off timing. |
| 3.37 | Self-Close Taps - Drinking Basins | Supply and install wall-type self-close taps on drinking basins, similar to existing. Work to include: removal of the existing tap, fitting of the new self-close mechanism, connection to supply, and testing of shut-off timing. |
| 3.38 | Kitchen Sink Accessories | Supply and install kitchen/cafeteria sink accessories (trap, angle valve, mixer), complete, similar to existing. Work to include: removal of failed components, fitting of new components, and testing for leaks. |
| 3.39 | Shower Head & Mixer Replacement | Supply and install new shower heads and mixers, complete, similar to existing. Work to include: removal of the existing fittings, connection of the new fittings to supply, and testing of flow and mixing operation. |
| 3.40 | Janitor Sink & Bathroom Accessories (JS) | Supply and install janitor sink and bathroom accessories (same sizing as existing): mixer, elbow trap, angle valves with flexible pipes, WC cover, tank accessories, and water heater. Work to include: removal of failed components, fitting of new components matching existing, and testing for leaks and correct operation. |
| 3.41 | Repair Option (Alt. 1) - Reinstate Relocated Drinking Fountains | Locate, recover and reinstall drinking fountains that were relocated from their original positions during the building's use as a shelter. Work to include: identifying and recovering each unit, reinstating it at its original position, reconnection to water supply and drain, and testing of flow and drainage. |
| 3.42 | Repair Option (Alt. 2) - Supply New Drinking Fountains (Missing/Damaged) | Supply, install, test and commission new drinking fountains at locations where the original unit is confirmed missing or beyond repair, similar to existing in type and finish. Work to include: fixing of the new unit, connection to water supply and drain, and testing of flow and drainage. |
| 3.43 | Rainwater Collection Tanks - Playground | Supply and install new 3,000-litre PE water tanks for playground rainwater collection, including connecting pipes with all accessories. Work to include: removal and disposal of failed tanks, fixing of new tanks, connection to collection and outlet pipework, and testing for leaks. |
| 3.44 | Electric Water Heater Replacement | Supply and install new electric water heater (100 L) serving the janitor's bathroom, similar to existing. Work to include: removal and disposal of the existing unit, fixing and electrical/plumbing connection of the new unit, and testing of safe operation. |
| 3.45 | Ramp-Top Stormwater Interception Drain (B3 & B4 Entry Ramps) | Supply and install a heavy-duty trench/channel drain with galvanized steel grating at the top of each basement vehicle ramp serving levels B3 and B4 (7m per ramp, 2 ramps), to intercept surface rainwater before it flows down into the basement. Work to include: excavation, drain channel and grating supply and installation, connection to an independent stormwater outfall (NOT the sanitary/sewage line, to avoid cross-contamination and backflow risk), and all sealing and making-good of the surrounding pavement: Asphalt layer (new subbase + base + asphalt). The works include sub-base and base preparation, prime/tack coat, laying and compaction to 5 cm after rolling, and reinstatement to match existing. |
| 3.46 | Flood Barriers, Backflow Valves & Sealing (B3 & B4 Entries + Drainage) | Supply and install remaining flood-protection measures at basement levels B3 and B4, in addition to the ramp-top interception drain above. Work to include: raised/flood-resistant thresholds or removable flood barriers at basement vehicle and pedestrian entrances; backflow-prevention (non-return) valves on all drainage/sewage lines serving the affected levels, to stop surcharged municipal sewers pushing water back into the building; and sealing of any identified wall/slab penetrations or construction joints found to be a water entry path. To be coordinated with the Lot 1 post-vacancy condition survey and the existing sump/submersible pump capacity at B1. |
| 3.47 | Potable Water Treatment Station - Rehabilitation | Rehabilitate the potable water treatment station, repairing identified damage and replacing damaged components to ensure a fully integrated operating system, regardless of which drinking-fountain option (below) is selected. Work to include: sand filter; carbon filter; RO unit ; cartridge filter (5 micron); UV steriliser; booster pumps; and stainless steel tank, each replaced/repaired as required and tested for correct operation. |
| 3.48 | Alternate Alt 3 - Remove All Drinking Fountains & Make Good Walls (In Lieu of Repair Option Items Above) | As an alternate to the Repair Option items above: remove all existing drinking fountains (56 no. building-wide) complete with all accessories and connections, cap off water supply and drain safely, and make good the wall finish (plaster, paint/tiling to match surrounding surfaces) at each vacated location. |

| Item number | Item/Milestone Required | Detailed Specifications and Requirements |
| --- | --- | --- |
| 4.1 | Solar Inverter Room - Access & Inspection | Gain access to, inspect and test the On-Grid solar system inverter room, currently inaccessible, and confirm correct operation of the inverter. Work to include: safe access/entry to the locked room, visual and functional inspection of the inverter and associated switchgear, and a written report of findings to the LRC Engineer. |
| 4.2 | Remove Temporary Cabling & Reinstate Proper Connection | Remove the temporary electrical cable extension installed to run water heaters for displaced persons, and reinstate a proper, code-compliant permanent connection/isolation as per the original design. Work to include: safe isolation and removal of the temporary cabling, making good any surfaces disturbed, and reinstatement of the circuit to its original, correctly protected configuration. |
| 4.3 | Fixing and Repairing - General Cables, Wires, Panels | Check and repair all existing cables, wires, sockets, outlets, electrical panel boards and circuit breakers, then prepare the suitable location to reinstall. Work to include: visual and continuity testing of accessible circuits, repair or replacement of damaged cabling/accessories, and confirmation of correct, safe operation prior to closing up. |
| 4.4 | Disconnecting Switches - 4x63A 4-Pole Waterproof (Basement) | Supply and install new disconnecting switch, 4 x 63A, 4-pole, waterproof-rated, located in the basement, similar to existing. Work to include: removal of the failed unit, fixing and wiring of the new switch, and testing of isolation function. |
| 4.5 | Disconnecting Switches - 4x40A 4-Pole Waterproof (Basement) | Supply and install new disconnecting switch, 4 x 40A, 4-pole, waterproof-rated, located in the basement, similar to existing. Work to include: removal of the failed unit, fixing and wiring of the new switch, and testing of isolation function. |
| 4.6 | Electrical Sockets - 16A Simplex 2P+E | Supply and install new 16 Amp Simplex Socket, 2P+E, similar to existing, complete with back box, wiring to the nearest suitable point, and cover plate. |
| 4.7 | Electrical Sockets - 16A Simplex Waterproof | Supply and install new 16 Amp Simplex Socket, waterproof-rated, similar to existing, complete with back box, wiring to the nearest suitable point, and weatherproof cover. |
| 4.8 | Electrical Sockets - 16A Simplex UPS Socket | Supply and install new 16 Amp Simplex UPS socket, 2P+E, similar to existing, complete with back box, dedicated wiring to the UPS distribution circuit, and cover plate. |
| 4.9 | Switches - 10A One Way One Gang | Supply and install new 10 AMP switch, one way, one gang, similar to existing, complete with back box, wiring and cover plate. |
| 4.10 | Switches - 10A One Way Two Gangs | Supply and install new 10 AMP switch, one way, two gangs, similar to existing, complete with back box, wiring and cover plate. |
| 4.11 | Switches - 10A Two Ways One Gang | Supply and install new 10 AMP switch, two ways, one gang, similar to existing, complete with back box, wiring and cover plate. |
| 4.12 | Switches - 10A Two Ways Two Gangs | Supply and install new 10 AMP switch, two ways, two gangs, similar to existing, complete with back box, wiring and cover plate. |
| 4.13 | Staircase Light Push-Button (Minuterie) | Supply and install new 10 AMP staircase light push-button switch for minuterie control, similar to existing, complete with back box, wiring and cover plate, and tested for correct timed operation. |
| 4.14 | Lighting Fixtures - TYPE B Twin T8 LED (Replace Complete) | Supply and install TYPE B lighting fixture, replacing the complete existing fixture with new: Twin T8 LED tube, surface-mount luminaire for interior use, 120cm, 40W - 4000K - 4700Lm, polycarbonate light grey colour, injected polyurethane double gasket, cover in clear UV-stabilised polycarbonate, cosφ ≥ 0.9. Work to include: removal and disposal of the existing fixture, fixing and wiring of the new fixture, and testing of correct illumination. |
| 4.15 | Lighting Fixtures - TYPE B Tube Replacement Only | Supply and replace only the T8 tubes in existing TYPE B lighting fixtures, similar to existing specification, complete with testing of correct illumination on completion. |
| 4.16 | Lighting Fixtures - TYPE A 120cm LED Panel (Classroom) | Supply and install TYPE A 120 cm LED panel for classrooms, similar to existing. Work to include: removal and disposal of the existing fixture, fixing and wiring of the new panel, and testing of correct illumination. |
| 4.17 | Lighting Fixtures - TYPE A1 LED Panel (Corridor) | Supply and install TYPE A1 LED panel, 3600lm - 33W - 4000K - 80CRI, surface-mount/recessed, die-cast aluminum, IP20, 600 x 600mm, for corridors. Work to include: removal and disposal of the existing fixture, fixing and wiring of the new panel, and testing of correct illumination. |
| 4.18 | Lighting Fixtures - TYPE H Round Spot (Ground Floor) | Supply and install TYPE H round spot with E27 holder, for the Ground Floor, similar to existing. Work to include: removal and disposal of the existing fixture, fixing and wiring of the new fixture, and testing. |
| 4.19 | Lighting Fixtures - E27 LED 14W | Supply and install LED light, E27 fitting, 14W, similar to existing. Work to include: removal and disposal of the existing lamp/fixture as applicable, fixing and wiring, and testing of correct illumination. |
| 4.20 | Lighting Fixtures - TYPE CC Twin T8 LED (WC) | Supply and install TYPE CC Twin T8 LED tube, recessed-mounted luminaire, for WC areas, similar to existing. Work to include: removal and disposal of the existing fixture, fixing and wiring of the new fixture, and testing of correct illumination. |
| 4.21 | Lighting Fixtures - TYPE M Motion-Sensor LED | Supply and install TYPE M LED fixture, 1500lm - 17W - 4000K - 80CRI, ceiling-mounted, with integral motion sensor, similar to existing. Work to include: removal and disposal of the existing fixture, fixing and wiring of the new fixture, and testing of sensor operation and illumination. |
| 4.22 | Lighting Fixtures - Emergency (Replace Existing EM) | Supply and install new LED emergency light fixture to replace each existing emergency (EM) fixture. Work to include: removal and disposal of the existing unit, fixing and wiring of the new fixture on the emergency circuit, and testing of battery back-up operation. |
| 4.23 | Lighting Fixtures - Exit Signs (Replace Existing) | Supply and install new LED exit sign to replace each existing exit sign. Work to include: removal and disposal of the existing unit, fixing and wiring of the new sign on the emergency circuit, and testing of illumination and battery back-up operation. |
| 4.24 | Test UPS System (No Replacement) | Test the existing Uninterruptible Power Supply (UPS 10 KVA) system to confirm it is functioning correctly and operating within acceptable parameters. Work to include: functional testing under load, battery-backup duration check, and a written report of findings and any deficiencies to the LRC Engineer. Battery replacement is excluded from this item. |
| 4.25 | Replace Damaged Photovoltaic Panels (600W) | Remove damaged/broken 600W multi-crystalline photovoltaic panels and supply, install and reconnect new panels matching existing specification. Work to include: safe isolation of the affected string, removal and disposal of damaged panels, fixing of new panels to the existing mounting structure, re-wiring, and testing of the affected string(s) for correct output. Quantity per the original Ministry design's surveyed count of damaged panels. |
| 4.26 | Rooftop Access / Working-at-Height Provision | Provide safe access (scaffolding/MEWP/fall-arrest system as applicable) for rooftop electrical and solar works, for the duration of those works, complete with all necessary certification and safety supervision. |
| 4.27 | Parking Management System - Test Only (No Repair) | Test the electrical and control wiring for the car-parking management system (automatic barriers/gates, car-counting system, card readers) once power supply is confirmed. Work to include: functional testing of each component, and a written report of any faults found to the LRC Engineer. Repair works are excluded from this item and, if required, will be scoped separately. |
| 4.28 | Replace Damaged Cabling - Lighting & Power Circuits, Flooded Basement Levels (B3 40% + B4 100%) | Remove and replace damaged lighting and general power circuit cabling within basement level B4 (fully flooded, 2,200 m²) and the flooded portion of basement level B3 (880 m²), following exposure to flood/sewage water. Work to include: safe isolation, removal and disposal of contaminated cabling and accessories, supply and installation of new cabling in accordance with applicable electrical codes, and full testing/certification prior to re-energization. Scope excludes B1 and B2 (unaffected). |
| 4.29 | Replace Feeder Cables to Pumps & Panels - Flooded Basement Levels | Remove and replace feeder cables serving pumps and distribution panels located within the flooded portions of basement levels B3 and B4. Work to include: safe isolation, removal and disposal of contaminated feeder cabling, supply and installation of new feeder cables sized to the connected load, and testing and reconnection to each piece of equipment. |
| 4.30 | Electrical Reconnection & Testing - Mechanical Equipment | Carry out electrical reconnection, control-wiring and testing of mechanical equipment rehabilitated under the Mechanical Works Lot, including pumps (submersible, booster, fire), exhaust fans and generator-room safety systems (fire suppression, dampers, solenoid valves). Work to include: reinstatement of power and control wiring to each item of equipment, functional testing, and linking of relevant systems to the fire alarm system where applicable. |
| 4.31 | Earthing System - Testing | Test the earthing system to confirm perfect operating condition, including the earth pits, earth test links, earth bars, and earth continuity conduits to all panels and motors. Work to include all civil works and earthing of all low-current systems as per specifications, with a written test report on completion. |
| 4.32 | Lightning Protection System | Rehabilitate and test the complete lightning protection system to ensure safety, comprising a Franklin rod at roof level with copper stranded bare conductor (3 x 25 mm) and all accessories and connections to the ground earth network. Work to include: inspection and repair of the air terminal, down-conductors and earth connections, continuity testing, and a written test report on completion. |
| 4.33 | Hybrid Inverter system upgrade | Supply, install, test and commission a hybrid inverter ,with similar capacity of the existing on-grid inverter, to provide backup power to critical loads (emergency/basement lighting, fire and water pumps) during grid or generator outages. Work to include: the inverter unit, automatic transfer/changeover switchgear, DC and AC wiring, protection devices, labelling, and full testing and commissioning with a written handover report. |
| 4.34 | Distribution Boards - Testing & Certification | Carry out general testing and certification of low-voltage distribution boards throughout the building. Work to include: visual inspection, insulation resistance and continuity testing, verification of correct labelling, and issue of a test certificate for each board. |
| 4.35 | Final Testing & Handover Certification | Carry out final testing and certification of all repaired/reconnected circuits and systems prior to handover. Work to include: functional testing of each system, compilation of test results, and preparation of as-built documentation for the LRC Engineer. |