National tender application pack V0.3Lebanese Red Cross 

Tender reference: 2026-092
VERSION 2
[bookmark: _Toc459799307]Annex 2 – Bid Form completed signed and stamped
· All bids must be typed; handwritten bids will not be considered.
· The contract will be awarded to the lowest-cost technically compliant complete lot or complete bid. 
· The quantities mentioned below are required unless there is a variation within a specified range with proper justification. The LRC reserves the right to increase or decrease the quantities.
· The bidder is not permitted to alter the section labelled “LRC to complete” below. Bidder is not allowed to use any other template.  
· In the event of any discrepancy between the unit price and the total price, LRC reserves the right to rely on the unit price as stated in the financial bid, rather than the total price without go back to the supplier. The unit price must be provided with no more than two decimal places.
· Only one option is allowed for biding 
· The bidder shall price each of the three distribution-line schedules separately. All unit rates shall include labor, materials, equipment, transport, testing, permits, overheads, incidental works, and all obligations necessary for the complete execution and handover of the works.
LOT 1:  Site Cleaning, Mobilization & Basement Desludging (B1-B4)
	LRC To Complete
	Bidder To Complete

	Item number 
	Item/Milestone Required
	Required UOM
	Estimated Qty
	Unit Price in USD, Exclusive VAT 
	VAT (%)
	Unit Price in USD, inclusive VAT 
	Total Price in USD, inclusive VAT 

	1.1
	Mobilization & Site Establishment
	L.S.
	1
	 
	 
	 
	 

	1.2
	Cleaning ,Disinfection & Sanitization  and disposal- All Occupied Spaces
	L.S.
	1
	 
	 
	 
	 

	1.3
	Parking-Level Drain & Channel Clearing (All Basement Levels)
	L.S.
	1
	 
	 
	 
	 

	1.4
	Post-Vacancy Condition Survey - Whole School (incl. Basement Levels)
	L.S.
	1
	 
	 
	 
	 





LOT 2:  Architectural & Civil Works
	LRC To Complete
	Bidder To Complete

	Item number 
	Item/Milestone Required
	Required UOM
	Estimated Qty
	Unit Price in USD, Exclusive VAT 
	VAT (%)
	Unit Price in USD, inclusive VAT 
	Total Price in USD, inclusive VAT 

	2.1
	Patch Exterior Wall Openings (Former A/C Sleeves) - Both Faces
	No.
	20
	 
	 
	 
	 

	2.2
	Localized Wall Plaster & Paint Repair (Moisture Damage)
	m2
	950
	 
	 
	 
	 

	2.3
	Crack Repair Below Classroom Windows
	No.
	35
	 
	 
	 
	 

	2.4
	Refinish Existing Powder-Coated Steel Door Frames
	No.
	300
	 
	 
	 
	 

	2.5
	Replace Severely Corroded Steel Door Frames
	No.
	16
	 
	 
	 
	 

	2.6
	Treat/Replace Emergency Push-Bar Hardware
	No.
	20
	 
	 
	 
	 

	2.7
	Repair/Replace Damaged Door Metal Fittings
	No.
	60
	 
	 
	 
	 

	2.8
	Repair Door Leaves & Hardware (Wood, Handles) - Classrooms, Toilets & Offices Only
	No.
	43
	 
	 
	 
	 

	2.9
	Reinstate Missing Wall-Mounted Stair Handrails
	m
	110
	 
	 
	 
	 

	2.10
	Rehabilitate & Maintain Wall-Mounted Steel Handrail (Existing)
	m
	350
	 
	 
	 
	 

	2.11
	Rehabilitate & Maintain Above-Parapet Steel Handrail (Existing)
	m
	350
	 
	 
	 
	 

	2.12
	Grind, Polish & Clean Marble Stair Treads
	m
	140
	 
	 
	 
	 

	2.13
	Replace Missing Bathroom Mirrors
	No.
	35
	 
	 
	 
	 

	2.14
	Clean, Secure & Reinstall Suspended Ceiling Strips
	m2
	200
	 
	 
	 
	 

	2.15
	Localized Ceiling Repaint
	m2
	180
	 
	 
	 
	 

	2.16
	Wall & Ceiling Paint - Super Rubber Paint (Old Walls/Ceilings)
	m2
	9800
	 
	 
	 
	 

	2.17
	Wall & Ceiling Paint - Oil Paint (Old Walls/Ceilings)
	m2
	5600
	 
	 
	 
	 

	2.18
	Treat & Clean Fairfaced Concrete Ceiling and Walls
	m2
	1400
	 
	 
	 
	 

	2.19
	Outside Walls Paint (Existing Walls and Ceilings)
	m2
	3500
	 
	 
	 
	 

	2.20
	Paint Damp-Proof Colourless Layer (Unleaded) on Facades
	m2
	3500
	 
	 
	 
	 

	2.21
	Replace Guard-Room Exterior Door
	No.
	1
	 
	 
	 
	 

	2.22
	Replace Guard-Room Toilet Door
	No.
	1
	 
	 
	 
	 

	2.23
	Replace Guard-Room Kitchen Counter
	m
	2
	 
	 
	 
	 

	2.24
	Clean & Re-point Sanitary Area Tiling
	m2
	500
	 
	 
	 
	 

	2.25
	New Curbstone
	m
	15
	 
	 
	 
	 

	2.26
	Rehabilitate Existing Curbstone
	m
	200
	 
	 
	 
	 

	2.27
	Rehabilitate Precast Concrete Tiles (Covered Playgrounds)
	m2
	15
	 
	 
	 
	 

	2.28
	New Timber Door (Single Leaf)
	No.
	3
	 
	 
	 
	 

	2.29
	New Timber Door with View Frame
	No.
	8
	 
	 
	 
	 

	2.30
	New Steel Double-Leaf Door
	No.
	1
	 
	 
	 
	 

	2.31
	Repair of Existing Aluminum Windows & Replace Broken Glass
	m2
	10
	 
	 
	 
	 

	2.32
	Tiling Works - Classroom & Corridor Ceramic (60x60cm)
	m2
	85
	 
	 
	 
	 

	2.33
	Tiling Works - Kitchen & Toilet Ceramic (30x60 or 30x30cm)
	m2
	5
	 
	 
	 
	 

	2.34
	Tiling Works - Laboratory Ceramic (60x60cm, Anti-Acid)
	m2
	5
	 
	 
	 
	 

	2.35
	Tiling Works - Skirting
	m
	5
	 
	 
	 
	 

	2.36
	Repair Existing Broken Floor Tiles & Skirting (All Types)
	L.S.
	1
	 
	 
	 
	 

	2.37
	Colored P.V.C. Flooring for KG Classrooms
	L.S.
	1
	 
	 
	 
	 

	2.38
	Handicapped Bathroom Accessories - Vertical Grab Rail
	No.
	2
	 
	 
	 
	 

	2.39
	Handicapped Bathroom Accessories - Horizontal Grab Rail
	No.
	2
	 
	 
	 
	 

	2.40
	Handicapped Bathroom Accessories - Drop-Down Removable Arm Rail
	No.
	2
	 
	 
	 
	 

	2.41
	Handicapped Bathroom Accessories - Emergency Alarm Pull Cord
	No.
	2
	 
	 
	 
	 

	2.42
	Epoxy Floor - Concrete Benches (Different Colours)
	m
	36
	 
	 
	 
	 

	2.43
	Signage
	No.
	240
	 
	 
	 
	 


LOT 3:  Mechanical Works
	LRC TO COMPLETE
	BIDDERS TO COMPLETE

	Item number 
	Item/Milestone Required
	Required UOM
	Estimated Qty
	Unit Price in USD, Exclusive VAT 
	VAT (%)
	Unit Price in USD, inclusive VAT 
	Total Price in USD, inclusive VAT 

	3.1
	LAV for Non-Kids - Taps, P-Traps & Angle Valves
	No.
	96
	 
	 
	 
	 

	3.2
	WC for Non-Kids - Seat Covers, Flushing Hoses & Tank Accessories
	No.
	84
	 
	 
	 
	 

	3.3
	Water Tank Leak Treatment
	No.
	2
	 
	 
	 
	 

	3.4
	Float Valves
	No.
	10
	 
	 
	 
	 

	3.5
	Roof Drains
	No.
	9
	 
	 
	 
	 

	3.6
	Vertical Pipes Fixation at Top of Roof Level
	No.
	10
	 
	 
	 
	 

	3.7
	Water Pipe Connection at Roof Level
	No.
	1
	 
	 
	 
	 

	3.8
	Flushing & Leak Test - Drainage and Water Pipes
	item
	1
	 
	 
	 
	 

	3.9
	Flushing & Gravity Test - Manholes
	item
	1
	 
	 
	 
	 

	3.10
	Floor Drain Covers
	No.
	60
	 
	 
	 
	 

	3.11
	Trench Drain + Rust Treatment/Paint
	m2
	5
	 
	 
	 
	 

	3.12
	Parking Drain + Rust Treatment/Paint
	m2
	5
	 
	 
	 
	 

	3.13
	Parking & Mechanical Rooms - Pipes
	Lm
	1
	 
	 
	 
	 

	3.14
	Parking & Mechanical Rooms - Ducts
	Lm
	10
	 
	 
	 
	 

	3.15
	Parking & Mechanical Rooms - Grilles/Registers
	No.
	1
	 
	 
	 
	 

	3.16
	Parking & Mechanical Rooms - Sprinklers
	No
	1
	 
	 
	 
	 

	3.17
	Parking Exhaust Fans - Mechanical Rehabilitation & Testing
	No.
	4
	 
	 
	 
	 

	3.18
	Transfer Booster Pump (B4) - Replacement & Testing
	No.
	2
	 
	 
	 
	 

	3.19
	Submersible Pumps + Sump Pits - Replacement Rehabilitation & Testing
	Set
	3
	 
	 
	 
	 

	3.20
	Transfer Booster Pumps (B1) - Replacement & Testing
	No.
	1
	 
	 
	 
	 

	3.21
	Water tank, and connections (B1) set
	Set
	1
	
	
	
	

	3.22
	Generator Rooms - Ventilation System (Mechanical inspection repair not included
	No.
	3
	 
	 
	 
	 

	3.23
	Generator Rooms - Pipes Insulation
	Lm
	1
	 
	 
	 
	 

	3.24
	Generator Rooms – Oil and Oil Filter Replacement
	No.
	3
	 
	 
	 
	 

	3.25
	Exhaust Fans - Testing
	No.
	41
	 
	 
	 
	 

	3.26
	Replace Broken Kids WC (K.G.)
	No.
	6
	 
	 
	 
	 

	3.27
	Replace Broken Non-Kids WC
	No.
	5
	 
	 
	 
	 

	3.28
	Replace Broken Kids Lavatories (K.G.)
	No.
	6
	 
	 
	 
	 

	3.29
	Replace Broken Non-Kids Lavatories
	No.
	5
	 
	 
	 
	 

	3.30
	Self-Close Taps - Kids & Students Lavatories
	No.
	14
	 
	 
	 
	 

	3.31
	Self-Close Taps - Drinking Basins
	No.
	12
	 
	 
	 
	 

	3.32
	Kitchen Sink Accessories
	No.
	3
	 
	 
	 
	 

	3.33
	Shower Head & Mixer Replacement
	No.
	2
	 
	 
	 
	 

	3.34
	Janitor Sink & Bathroom Accessories (JS)
	No.
	8
	 
	 
	 
	 

	3.35
	Repair Option (Alt. 1) - Reinstate Relocated Drinking Fountains
	No.
	40
	 
	 
	 
	 

	3.36
	Repair Option (Alt. 2) - Supply New Drinking Fountains (Missing/Damaged)
	No.
	16
	 
	 
	 
	 

	3.37
	Alternate Alt 3 - Remove All Drinking Fountains & Make Good Walls (In Lieu of Repair Option Items Above)
	No.
	56
	 
	 
	 
	 

	3.38
	Electric Water Heater Replacement
	No.
	1
	 
	 
	 
	 

	3.39
	Potable Water Treatment Station - Rehabilitation on the Roof
	No.
	1
	 
	 
	 
	 



LOT 4:  Electrical Works
	LRC TO COMPLETE
	BIDDERS TO COMPLETE

	Item number 
	Item/Milestone Required
	Required UOM
	Estimated Qty
	Unit Price in USD, Exclusive VAT 
	VAT (%)
	Unit Price in USD, inclusive VAT 
	Total Price in USD, inclusive VAT 

	4.1
	Hybrid Inverter system upgrade
	Lot
	1
	 
	 
	 
	 

	4.2
	Remove Temporary Cabling & Reinstate Proper Connection 2-4 mm
	Lm.
	10
	 
	 
	 
	 

	4.3
	Remove Temporary Cabling & Reinstate Proper Connection 6-10 mm
	Lm.
	10
	
	
	
	

	4.4
	Remove Temporary Cabling & Reinstate Proper Connection 10 25 mm
	Lm.
	10
	
	
	
	

	4.5
	Fixing and Repairing - General Cables, Wires, Panels
	No.
	2
	 
	 
	 
	 

	4.6
	Control panels for submersible pumps
	No.
	2
	
	
	
	

	4.7
	Disconnecting Switches - 4x63A 4-Pole Waterproof (Basement)
	No.
	2
	 
	 
	 
	 

	4.8
	Disconnecting Switches - 4x40A 4-Pole Waterproof (Basement)
	No.
	6
	 
	 
	 
	 

	4.9
	Electrical Sockets - 16A Simplex 2P+E
	No.
	40
	 
	 
	 
	 

	4.10
	Electrical Sockets - 16A Simplex Waterproof
	No.
	20
	 
	 
	 
	 

	4.11
	Electrical Sockets - 16A Simplex UPS Socket
	No.
	10
	 
	 
	 
	 

	4.12
	Switches - 10A One Way One Gang
	No.
	16
	 
	 
	 
	 

	4.13
	Switches - 10A One Way Two Gangs
	No.
	16
	 
	 
	 
	 

	4.14
	Switches - 10A Two Ways One Gang
	No.
	6
	 
	 
	 
	 

	4.15
	Switches - 10A Two Ways Two Gangs
	No.
	6
	 
	 
	 
	 

	4.16
	Staircase Light Push-Button (Minuterie)
	No.
	20
	 
	 
	 
	 

	4.17
	Lighting Fixtures - TYPE B Twin T8 LED (Replace Complete)
	No.
	100
	 
	 
	 
	 

	4.18
	Lighting Fixtures - TYPE B Tube Replacement Only
	No.
	200
	 
	 
	 
	 

	4.19
	Lighting Fixtures - TYPE A 120cm LED Panel (Classroom)
	No.
	50
	 
	 
	 
	 

	4.20
	Lighting Fixtures - TYPE A1 LED Panel (Corridor)
	No.
	50
	 
	 
	 
	 

	4.21
	Lighting Fixtures - TYPE H Round Spot (Ground Floor)
	No.
	8
	 
	 
	 
	 

	4.22
	Lighting Fixtures - E27 LED 14W
	No.
	50
	 
	 
	 
	 

	4.23
	Lighting Fixtures - TYPE CC Twin T8 LED (WC)
	No.
	10
	 
	 
	 
	 

	4.24
	Lighting Fixtures - TYPE M Motion-Sensor LED
	No.
	10
	 
	 
	 
	 

	4.25
	Lighting Fixtures - Emergency (Replace Existing EM)
	No.
	50
	 
	 
	 
	 

	4.26
	Lighting Fixtures - Exit Signs (Replace Existing)
	No.
	10
	 
	 
	 
	 

	4.27
	Test UPS System (No Replacement)
	No.
	1
	 
	 
	 
	 

	4.28
	Replace Damaged Photovoltaic Panels (600W)
	No.
	15
	 
	 
	 
	 

	4.29
	Parking Management System - Test Only (No Repair)
	No.
	1
	 
	 
	 
	 

	4.30
	Earthing System - Testing
	L.S.
	1
	 
	 
	 
	 

	4.31
	Lightning Protection System
	No.
	1
	 
	 
	 
	 

	4.32
	Distribution Boards - Testing & Certification And Final Testing & Handover Certification
	L.S.
	1
	 
	 
	 
	 




	Divisions
	Items by Trade
	Total
Exc (VAT)
	Total
(Inc VAT)

	Division 1
	Site Cleaning, Mobilization & Basement Desludging (B1-B4)
	
	

	Division 2
	Architectural & Civil Works
	
	

	Division 3
	Mechanical Works
	
	

	Division 4
	Electrical Works
	
	

	Grand Total                           






ANNEX 3: DETAILED SPECIFICATIONS 

As per: 2026-092 Terms of Reference

	LRC To Complete

	Item number 
	Item/Milestone Required
	Detailed Specifications and Requirements

	1.1
	Mobilization & Site Establishment
	Mobilize personnel, equipment, temporary site facilities, signage and safety barriers, and set up welfare and storage facilities for the duration of the works. Work to include: coordination of site access and working hours with the school administration and LRC Engineer; submission of a method statement and programme prior to start of works; and all labour, equipment and materials needed to establish the site, to the satisfaction of the Engineer.

	1.2
	Cleaning ,Disinfection & Sanitization  and disposal- All Occupied Spaces
	Clean al floors and Supply and apply approved disinfectant/sanitizing agents to all classrooms, rooms, offices, laboratories, WCs, corridors, terraces and balconies throughout the building (all basement levels, and Ground Floor to Floor 6, given the building's recent use as a displacement shelter. Work to include: all cleaning needs, disinfectant materials, application equipment and labour; surface disinfection of floors, walls (to hand height), door handles, sanitary fixtures and fittings; and appropriate PPE and ventilation during application, all to the satisfaction of the Engineer.

	1.3
	Parking-Level Drain & Channel Clearing (All Basement Levels)
	Clear accumulated debris from parking-area floor drains, trench drains and drainage channels across all four basement levels ahead of the mechanical rehabilitation works. Work to include: manual/mechanical removal of silt and debris from drain bodies and channels; confirmation that drains run free; and lawful disposal of removed material, to the satisfaction of the Engineer.

	1.4
	Post-Vacancy Condition Survey - Whole School (incl. Basement Levels)
	Following full vacancy of the school and completion of the cleaning and disinfection works, carry out and submit a detailed condition survey covering the ENTIRE building, not only the basement levels. Particular attention to be given to: (a) basement levels B3 and B4, to define the scope of any further finishes-repair works there; and (b) any classrooms, offices, stores or other rooms throughout the school that were previously occupied by displaced persons, kept locked, or otherwise inaccessible during the initial assessment, to identify any additional defects not visible at that time. Work to include: a room-by-room photographic record across all floors; a written assessment of floor, wall, door and MEP component condition; and a summary report identifying items requiring repair, submitted to the LRC Engineer for approval before any further works in the affected areas are instructed.









	Item number 
	Item/Milestone Required
	Detailed Specifications and Requirements

	2.1
	Patch Exterior Wall Openings (Former A/C Sleeves) - Both Faces
	Cut back, fill and make good 20 no. openings (10 cm radius) left in the exterior walls from temporary air-conditioning unit installations, accessed and finished from BOTH the interior and exterior faces. Work to include: cutting back and cleaning the opening; cement mortar fill; render reinstatement to match existing texture; paint finish matching existing colour on both sides; and any scaffolding, ladders or rope access equipment required for exterior work above ground level, to the satisfaction of the Engineer.

	2.2
	Localized Wall Plaster & Paint Repair (Moisture Damage)
	Rehabilitate and repair cracked and damaged plaster in indoor and outdoor areas. Work to include: determine the location and remove all loose material around the area; remove the cracked plaster layer; install galvanized steel mesh (20 cm width minimum); clean the affected areas with suitable materials; reinstate plaster and apply paint finish to match existing colour and texture. Priority to lower wall sections above skirting and former drinking-fountain locations, where deterioration is linked to moisture/water presence, all as per specifications and Engineer's instructions.

	2.3
	Crack Repair Below Classroom Windows
	Rehabilitate and repair cracks observed below windows in classrooms. Work to include: routing out and cleaning of the crack; filling with suitable crack-repair compound; reinstatement of plaster; and repainting of the affected area to match existing colour and finish, all to the satisfaction of the Engineer.

	2.4
	Refinish Existing Powder-Coated Steel Door Frames
	Refinish existing powder-coated steel door frames to restore an as-new appearance, representing the majority of frames assessed to be in serviceable condition. Work to include: on-site surface preparation (sanding/etching/degreasing); application of a 2-pack enamel or equivalent system compatible with the existing powder-coat finish; and colour-matching to existing. Full factory re-powder-coating is not required.

	2.5
	Replace Severely Corroded Steel Door Frames
	Supply and install new steel door frames matching existing size, type and finish, at locations where the existing frame is found to be severely corroded beyond repair, particularly in toilet areas. Work to include: removal and disposal of the existing frame; making good the surrounding wall/reveal finish; supply and fixing of the new frame with all related accessories; and finishing paint, all as per specifications.

	2.6
	Treat/Replace Emergency Push-Bar Hardware
	Clean and apply anti-rust treatment to emergency/panic push-bar hardware on stair doors showing light surface rust, and confirm smooth operation. Work to include: full replacement of the push-bar unit, with all fixings, at locations where treatment alone is not sufficient to restore safe operation.

	2.7
	Repair/Replace Damaged Door Metal Fittings
	Repair or replace missing or damaged door metal fittings and accessories (hinges, closers, handles, locksets) at various locations throughout the building. Work to include: removal of damaged fittings; supply and fixing of new fittings of similar type and quality to existing; and adjustment to confirm smooth, safe operation of the door.

	2.8
	Repair Door Leaves & Hardware (Wood, Handles) - Classrooms, Toilets & Offices Only
	Repair damaged door leaves and hardware limited to classrooms, toilets/WCs and administrative offices only - corridors, staircases, labs, storerooms and mechanical/electrical rooms are excluded from this item. Work to include: repair of delaminated/water-damaged panels, edges and cores; replacement of damaged handles, hinges and locks; and re-hanging/adjustment for smooth operation, finished to match existing. Priority to toilet/WC cubicle and entry doors, followed by classroom and office doors, per the condition assessment findings.

	2.9
	Reinstate Missing Wall-Mounted Stair Handrails
	Supply and install new steel wall-mounted handrail at stairs, similar to existing in shape, form, length, finish and colour, at locations currently missing a handrail. Item to include labour, equipment, material and all works required to complete the works. Contractor to submit shop drawings and samples prior to installation, for the Engineer's approval.

	2.10
	Rehabilitate & Maintain Wall-Mounted Steel Handrail (Existing)
	Rehabilitate and maintain existing wall-mounted steel handrails at staircases and balconies, returning them to their original form and condition. Work to include: straightening and welding of loose, bent or detached sections; grinding and polishing of welded joints; anti-rust treatment; and repainting to match existing colour and finish, all as per specifications and to the Engineer's approval.

	2.11
	Rehabilitate & Maintain Above-Parapet Steel Handrail (Existing)
	Rehabilitate and maintain existing above-parapet steel handrails, returning them to their original form and condition. Work to include: straightening and welding of loose, bent or detached sections; grinding and polishing of welded joints; anti-rust treatment; and repainting to match existing colour and finish, all as per specifications and to the Engineer's approval.

	2.12
	Grind, Polish & Clean Marble Stair Treads
	Grind, polish and clean existing marble stair treads showing general wear, to restore a smooth, non-slip and presentable surface. Work to include: diamond grinding of the tread surface, polishing to a consistent finish matching adjacent treads, and final cleaning, all to the satisfaction of the Engineer.

	2.13
	Replace Missing Bathroom Mirrors
	Supply and install new mirrors at bathroom/lavatory locations found missing. Work to include: mirror glass with polished edges, dimensions as per site conditions; anti-corrosion wall-fixing hardware suitable for a humid environment; and sealing of edges,similar to the existing and according  to the Engineer's approval.

	2.14
	Clean, Secure & Reinstall Suspended Ceiling Strips
	Supply and install aluminum strip suspended ceiling as per specifications, and fix or replace any damaged part. Work to include: materials (aluminum sheet thickness similar to existing); labour; accessories; angles; and a heavy-duty metal suspension system, cleaned and secured throughout, similar to existing.

	2.15
	Localized Ceiling Repaint
	Rehabilitate and repaint ceiling areas including corridor soffits and stairwell void edges. Work to include: surface preparation (cleaning, filling of minor imperfections); application of primer where bare substrate is exposed; and two coats of finish paint matching existing colour, to the satisfaction of the Engineer.

	2.16
	Wall & Ceiling Paint - Super Rubber Paint (Old Walls/Ceilings)
	Supply and apply super rubber paint to old internal walls and ceilings. Work to include: surface preparation, filling of minor imperfections, primer where bare substrate is exposed, and two coats of finish paint, colour as directed by the Engineer. Quantity is 70% of the original design's building-wide allowance (14,000 m²), per LRC's phased-scope decision.

	2.17
	Wall & Ceiling Paint - Oil Paint (Old Walls/Ceilings)
	Supply and apply oil paint to old internal walls and ceilings. Work to include: surface preparation, primer where required, and two coats of finish paint, colour as directed by the Engineer. Quantity is 70% of the original design's building-wide allowance (8,000 m²), per LRC's phased-scope decision.

	2.18
	Treat & Clean Fairfaced Concrete Ceiling and Walls
	Treat and clean existing fairfaced (exposed) concrete ceiling and wall surfaces. Work to include: cleaning of surface contamination, minor patch repair, and application of an approved clear protective/sealing treatment to restore appearance. Quantity is 70% of the original design's building-wide allowance (2,000 m²), per LRC's phased-scope decision.

	2.19
	Outside Walls Paint (Existing Walls and Ceilings)
	Paint for external old and new walls, smooth touch. Work to include: removal of any loose paint or obstacles; rehabilitation of the surface and making it good; polyurethane sealant where needed for cracks; and application of 2 coats of exterior-grade paint. Quantity is 70% of the original design's building-wide allowance (5,000 m²), per LRC's phased-scope decision.

	2.20
	Paint Damp-Proof Colourless Layer (Unleaded) on Facades
	Supply and paint with damp-proof paint after cleaning and washing all walls; remove the existing paint and enlarge all cracks, especially at the intersection of hollow concrete blocks and reinforced concrete elements, prior to application. Quantity is 70% of the original design's building-wide allowance (5,000 m²), per LRC's phased-scope decision.

	2.21
	Replace Guard-Room Exterior Door
	Supply and install new external door for the guard room, found in poor condition, suitable for the security/access requirements of the location. Work to include: new door leaf and frame, all hardware (hinges, lockset, handle), and finishing paint to both faces of the door and box frame, similar to existing in size and function.

	2.22
	Replace Guard-Room Toilet Door
	Supply and install new solid single-leaf flush timber door similar to existing, with a minimum 10 cm wide frame between the plywood faces filled with timber beads (tongue and groove, each 5 cm), and door edges in bead wood fixed by tongue and groove frames, all as specified. Work to include all accessories and fittings (hinges, lockset, handle), and finishing paint to both faces of the door leaf and the box frame.

	2.23
	Replace Guard-Room Kitchen Counter
	Supply and install new marble worktop (counter) for the guard room's kitchenette, similar to existing in size, thickness and finish, to replace the damaged unit. Work to include: removal and disposal of the existing counter, supply and fixing of the new marble top with polished edges, and sealing to the adjoining cabinetry.

	2.24
	Clean & Re-point Sanitary Area Tiling
	General cleaning and re-pointing/grouting of wall and floor tiling and joints in bathroom areas throughout the building. Work to include: removal of degraded/discoloured grout, cleaning of tile surfaces, and reinstatement of grout/pointing matching existing colour, to a sound, hygienic finish.

	2.25
	New Curbstone
	Supply and install new precast fairfaced concrete curbstone as per specifications. Work to include: labour, material and equipment; curb fill and mortar; removal of existing damaged units; casting of concrete behind the curbstone; and handicapped concrete units where required. All works as per specifications and Engineer's instructions.

	2.26
	Rehabilitate Existing Curbstone
	Inspect and rehabilitate existing curbstone as per specifications. Work to include: removal of all loose or damaged parts and re-installation as existing; materials; and cleaning. All works as per specifications and Engineer's instructions.

	2.27
	Rehabilitate Precast Concrete Tiles (Covered Playgrounds)
	Supply and install precast concrete tiles similar to existing. Samples to be provided for approval. Work to include: labour, material and equipment; the necessary fill below tiles; and installation of tiles, all as per specifications and Engineer's instructions.

	2.28
	New Timber Door (Single Leaf)
	Supply and install flush timber door with laminated plastic facing. The door shall have a 10 cm wide frame between the plywood, filled with timber beads by tongue and groove (each 5 cm), and the door edges shall be bead wood, fixed by tongue and groove frames, all as specified. Work to include all accessories and fittings, pre-painting and finishing paint to both sides of the door and box frame.

	2.29
	New Timber Door with View Frame
	As Item 2.28 (flush timber door with laminated plastic facing, 10 cm frame, timber bead tongue-and-groove construction, all accessories, fittings and finishing paint), with the addition of a vision/view frame (glazed panel) incorporated into the door leaf, as per specifications.

	2.30
	New Steel Double-Leaf Door
	Supply and install new steel double-leaf door with related accessories, similar to existing, as per specifications. Work to include: two door leaves, frame, all hardware (hinges, lockset, handle) and finishing paint to both faces of the door leaves and box frame.

	2.31
	Repair of Existing Aluminum Windows & Replace Broken Glass
	Repair existing aluminum windows and replace broken glass throughout the building. Work to include: checking the functionality of latches, hinges and other hardware, and replacing broken parts with new ones so each window operates smoothly; removal and replacement of cracked/broken glass panes to match existing type and thickness; and application of a high-quality sealant around all edges to prevent moisture ingress, with all associated finishing works.

	2.32
	Tiling Works - Classroom & Corridor Ceramic (60x60cm)
	Supply and install anti-skid coloured ceramic tiles, 60 x 60 cm, first choice, for classrooms and corridors. Work to include: surface preparation, bedding mortar, tile laying to true line and level, and grouting to match tile colour & similar to the existing.

	2.33
	Tiling Works - Kitchen & Toilet Ceramic (30x60 or 30x30cm)
	Supply and install anti-skid coloured ceramic tiles, 30 x 60 cm or 30 x 30 cm, for kitchens and toilets. Work to include: surface preparation, bedding mortar, tile laying to true line and level, and grouting to match tile colour& similar to the existing .

	2.34
	Tiling Works - Laboratory Ceramic (60x60cm, Anti-Acid)
	Supply and install anti-acid and anti-skid coloured ceramic tiles, 60 x 60 cm, for laboratories. Work to include: surface preparation, bedding mortar, tile laying to true line and level, and chemical-resistant grouting& similar to the existing.

	2.35
	Tiling Works - Skirting
	Supply and install skirting tiles to match flooring finish (10 cm height), same type and matching colour as the ceramic floor tiles, neatly fixed and grouted to the wall/floor junction.

	2.36
	Repair Existing Broken Floor Tiles & Skirting (All Types)
	Inspect the entire floor area, then rehabilitate and repair all damaged and broken tiles and skirting of any type (marble, ceramic, mosaic, cement). Work to include: removal of all debris as specified; all materials and labour; matching of tile shape, thickness, dimension and pattern to existing; and reinstatement similar to existing, for all rooms and corridors, to the Engineer's approval.

	2.37
	Colored P.V.C. Flooring for KG Classrooms
	Rehabilitate and clean existing coloured PVC flooring for KG classrooms. Work to include: cutting and patching of damaged areas (matching thickness, shape and colour); welding of joints; fixing of skirting; and general cleaning, with all works approved by the Engineer prior to installation.

	2.38
	Handicapped Bathroom Accessories - Vertical Grab Rail
	Supply and install vertical grab rail, 60 cm bars, complete with heavy-duty anti-corrosion fixings suitable for a wet environment, to the Engineer's approval.

	2.39
	Handicapped Bathroom Accessories - Horizontal Grab Rail
	Supply and install horizontal grab rail, 60 cm bars, complete with heavy-duty anti-corrosion fixings suitable for a wet environment, to the Engineer's approval.

	2.40
	Handicapped Bathroom Accessories - Drop-Down Removable Arm Rail
	Supply and install drop-down rail, removable arm, 80 cm, complete with heavy-duty anti-corrosion fixings suitable for a wet environment, to the Engineer's approval.

	2.41
	Handicapped Bathroom Accessories - Emergency Alarm Pull Cord
	Supply and install alarm pull cord for emergency use, wired to the nurse/supervisor station, complete with all accessories and testing prior to handover.

	2.42
	Epoxy Floor - Concrete Benches (Different Colours)
	Supply and install epoxy with polyurethane layer finishing on existing concrete benches, different colours, suitable for playground use. Work to include: surface preparation and cleaning of the existing bench, filling of any cracks or chips, and application of the epoxy/polyurethane finish system to a durable, weather-resistant standard.

	2.43
	Signage
	Supply and install sliding panel signs for all rooms, high-pressure laminate (HPL) 1.2 cm thick, movable inside a stainless steel rail (316), fixed on walls, letters vinyl-printed with engravement for special-need purposes. Colours and shape as per Engineer's instruction. Dimension: 20cm x 10cm.





	Item number 
	Item/Milestone Required
	Detailed Specifications and Requirements

	3.1
	LAV for Non-Kids - Taps, P-Traps & Angle Valves
	Supply and install new taps, P-traps and angle valves with flexible pipe connections for non-kids lavatories throughout the building, similar to existing. Work to include: removal and disposal of the existing failed fittings, supply of new fittings of equivalent or better quality, connection to existing supply and waste points, and testing for leaks.

	3.2
	WC for Non-Kids - Seat Covers, Flushing Hoses & Tank Accessories
	Supply and install new seat covers, flushing hoses, tank accessories, and angle valves with flexible pipe connections for non-kids WCs throughout the building, similar to existing. Work to include: removal and disposal of failed components, fitting of new components, and testing of flush and shut-off operation.

	3.3
	Water Tank Leak Treatment
	Treat water leakage from the two existing 10,000-litre PE tanks located at roof level. Work to include: locating the source of leakage, cleaning and preparing the affected surface, application of an approved leak-sealing compound/patch suitable for potable water contact, and confirmation the tank holds water without leaking.

	3.4
	Float Valves
	Test and rehabilitate float valves at water tanks and cisterns to confirm correct shut-off operation. Work to include: removal of the existing valve where faulty, supply and fitting of a new valve of matching size/type, and testing of water level control.

	3.5
	Roof Drains
	Clean and rehabilitate roof drains located on the roof. Work to include: removal of debris and blockages, checking and repair of the drain body and strainer, and confirmation of free-flowing drainage.

	3.6
	Vertical Pipes Fixation at Top of Roof Level
	Reinstall and re-secure vertical water filling pipes at roof level in a proper technical manner. Work to include: supply of new pipe clips/brackets as required, correct alignment and fixing of pipework, and confirmation the installation is stable and watertight.

	3.7
	Water Pipe Connection at Roof Level
	Reinstate and reconnect water pipe connections at roof level, including a previously disconnected water pipe, as required. Work to include: supply of any missing fittings, jointing/sealing of connections, and pressure/leak testing on completion.

	3.8
	Flushing & Leak Test - Drainage and Water Pipes
	Carry out flushing and leak testing for the existing drainage and water pipes throughout the building. Work to include: flushing of all accessible lines to clear debris, pressure/gravity testing as applicable, identification of any leaks or blockages, and repair of any defects found to achieve a fully functioning system.

	3.9
	Flushing & Gravity Test - Manholes
	Carry out flushing and gravity testing for the existing manholes and related pipe connections. Work to include: opening and inspecting manholes, flushing connected pipe runs, confirming correct fall/gravity flow, and repair of any defects found.

	3.10
	Floor Drain Covers
	Supply and install new floor drain covers throughout the building, similar to existing, complete with cleaning of the drain body beneath each cover.

	3.11
	Trench Drain + Rust Treatment/Paint
	Clean and rehabilitate the trench drain at parking level. Work to include: removal of debris and silt, rust treatment of steel grating/frame, and repainting of steel parts to prevent further corrosion.

	3.12
	Parking Drain + Rust Treatment/Paint
	Clean and rehabilitate parking-level drain outlets. Work to include: removal of debris and silt, rust treatment of steel grating/frame, and repainting of steel parts to prevent further corrosion.

	3.13
	Parking & Mechanical Rooms - Pipes
	Carry out maintenance, rehabilitation, testing and commissioning of pipework within the parking and mechanical rooms. Work to include: inspection of all accessible pipe runs, repair or replacement of damaged sections, re-fixing of loose supports, and pressure testing on completion.

	3.14
	Parking & Mechanical Rooms - Ducts
	Carry out maintenance, rehabilitation, testing and commissioning of ductwork within the parking and mechanical rooms. Work to include: inspection of accessible ductwork, repair of damaged sections and joints, re-fixing of loose supports, and confirmation of correct airflow.

	3.15
	Parking & Mechanical Rooms - Grilles/Registers
	Carry out maintenance, rehabilitation, testing and commissioning of grilles and registers within the parking and mechanical rooms. Work to include: cleaning, repair or replacement of damaged grilles/registers, and confirmation of free operation of adjustable louvres.

	3.16
	Parking & Mechanical Rooms - Sprinklers
	Carry out maintenance, rehabilitation, testing and commissioning of the sprinkler system within the parking and mechanical rooms. Work to include: inspection of sprinkler heads and pipework, replacement of damaged/corroded heads, and flow testing to confirm the system is operational.

	3.17
	Parking Exhaust Fans - Mechanical Rehabilitation & Testing
	Mechanically rehabilitate and test parking-level exhaust fans, repairing identified mechanical faults. Work to include: inspection of fan blades, bearings and mounts; cleaning and lubrication; repair or replacement of faulty mechanical components; and confirmation of free rotation. Electrical connection/reconnection of the fans is covered under the Electrical Works Lot.

	3.18
	Transfer Booster Pump (B4) - Replacement & Testing
	Replace, and test the transfer booster pump located at B4. Work to include: replacement of pump with same capacity, and confirmation of correct mechanical operation, and electrical connections. With same capacity as existing and with European origins to be approved by LRC

	3.19
	Submersible Pumps + Sump Pits - Replacement & Testing
	Replace, and test submersible pumps and associated sump pits. Work to include: replacement of pump with same capacity,, cleaning and repair/replacement of sump pit covers, and confirmation of correct mechanical operation. and electrical connections. With same capacity as existing and with European origins to be approved by LRC

	3.20
	Transfer Booster Pumps (B1) - Replacment & Testing
	Replace, and test the transfer booster pump located at B4. Work to include: replacement of pump with same capacity, and confirmation of correct mechanical operation, and electrical connections. With same capacity as existing and with European origins to be approved by LRC

	3.21
	Water tank, and connections (B1) set
	Replace water tanks and connections at B1 up to the booster pumps similar to the existing setup same size and capacity

	3.22
	Generator Rooms - Ventilation System (Mechanical inspection repair not included)
	Mechanically check the ventilation system, interlocked with generator operation, for each of the three generator rooms. Work to include: inspection of louvres, dampers and ductwork, , and confirmation of airflow when the generator runs.

	3.23
	Generator Rooms - Pipes Insulation
	Repair pipe insulation within the generator rooms. Work to include: removal of damaged/degraded insulation, supply and fitting of new insulation matching existing thickness and type, and finishing with protective cladding where originally provided.

	3.24
	Generator Rooms – Oil and Oil Filter Replacement
	Supply and replace Oil and oil filters for the three generators, of the correct type and specification for each unit, with disposal of the used filters and oil in an environmentally sound manner.

	3.25
	Exhaust Fans - Testing 
	Test existing exhaust fans throughout the building. 

	3.26
	Replace Broken Kids WC (K.G.)
	Supply and install new WC (EWC, same sizing as existing) for the kindergarten, complete with all accessories, to replace units found broken. Work to include: removal and disposal of the broken unit, supply and fixing of the new unit, connection to existing supply and waste, and testing of flush operation.

	3.27
	Replace Broken Non-Kids WC
	Supply and install new WC (EWC, same sizing as existing) for non-kids areas, complete with all accessories, to replace units found broken. Work to include: removal and disposal of the broken unit, supply and fixing of the new unit, connection to existing supply and waste, and testing of flush operation.

	3.28
	Replace Broken Kids Lavatories (K.G.)
	Supply and install new wall-hung lavatory (45 x 35 cm) for kids in the K.G., complete with all accessories, to replace units found broken. Work to include: removal and disposal of the broken unit, supply and fixing of the new unit, connection to existing supply and waste, and leak testing.

	3.29
	Replace Broken Non-Kids Lavatories
	Supply and install new semi-pedestal lavatory with mixer (55 x 45 cm) for non-kids areas, complete with all accessories, to replace units found broken. Work to include: removal and disposal of the broken unit, supply and fixing of the new unit, connection to existing supply and waste, and leak testing.

	3.30
	Self-Close Taps - Kids & Students Lavatories
	Supply and install self-close taps on kids' and students' lavatories, similar to existing. Work to include: removal of the existing tap, fitting of the new self-close mechanism, connection to supply, and testing of shut-off timing.

	3.31
	Self-Close Taps - Drinking Basins
	Supply and install wall-type self-close taps on drinking basins, similar to existing. Work to include: removal of the existing tap, fitting of the new self-close mechanism, connection to supply, and testing of shut-off timing.

	3.32
	Kitchen Sink Accessories
	Supply and install kitchen/cafeteria sink accessories (trap, angle valve, mixer), complete, similar to existing. Work to include: removal of failed components, fitting of new components, and testing for leaks.

	3.33
	Shower Head & Mixer Replacement
	Supply and install new shower heads and mixers, complete, similar to existing. Work to include: removal of the existing fittings, connection of the new fittings to supply, and testing of flow and mixing operation.

	3.34
	Janitor Sink & Bathroom Accessories (JS)
	Supply and install janitor sink and bathroom accessories (same sizing as existing): mixer, elbow trap, angle valves with flexible pipes, WC cover, tank accessories, and water heater. Work to include: removal of failed components, fitting of new components matching existing, and testing for leaks and correct operation.

	3.35
	Repair Option (Alt. 1) - Reinstate Relocated Drinking Fountains
	Locate, recover and reinstall drinking fountains that were relocated from their original positions during the building's use as a shelter. Work to include: identifying and recovering each unit, reinstating it at its original position, reconnection to water supply and drain, and testing of flow and drainage.

	3.36
	Repair Option (Alt. 2) - Supply New Drinking Fountains (Missing/Damaged)
	Supply, install, test and commission new drinking fountains at locations where the original unit is confirmed missing or beyond repair, similar to existing in type and finish. Work to include: fixing of the new unit, connection to water supply and drain, and testing of flow and drainage.

	3.37
	Alternate Alt 3 - Remove All Drinking Fountains & Make Good Walls (In Lieu of Repair Option Items Above)

	As an alternate to the Repair Option items above: remove all existing drinking fountains (56 no. building-wide) complete with all accessories and connections, cap off water supply and drain safely, and make good the wall finish (plaster, paint/tiling to match surrounding surfaces) at each vacated location.

	3.38
	Electric Water Heater Replacement
	Supply and install new electric water heater (100 L) serving the janitor's bathroom, similar to existing. Work to include: removal and disposal of the existing unit, fixing and electrical/plumbing connection of the new unit, and testing of safe operation.

	3.39
	Potable Water Treatment Station - Rehabilitation 
	Rehabilitate the potable water treatment station, repairing identified damage and replacing damaged components to ensure a fully integrated operating system, regardless of which drinking-fountain option (below) is selected. Work to include: sand filter; carbon filter; RO unit ; cartridge filter (5 micron); UV steriliser; booster pumps; and stainless steel tank, each replaced/repaired as required and tested for correct operation.






	Item number 
	Item/Milestone Required
	Detailed Specifications and Requirements

	4.1
	Hybrid Inverter system upgrade
	Supply, install, test and commission a  hybrid inverter ,with similar capacity of the  existing on-grid inverter, to provide backup power to critical loads (emergency/basement lighting, fire and water pumps) during grid or generator outages. Work to include: the inverter unit, automatic transfer/changeover switchgear, DC and AC wiring, protection devices, all necessary control panel and units, labelling, and full testing and commissioning with a written handover report.

	4.2
	Remove Temporary Cabling & Reinstate Proper Connection 2-4 mm
	Remove the temporary electrical cable extension installed and reinstate a proper, code-compliant permanent connection/isolation as per the original design. Work to include: safe isolation and removal of the temporary cabling, making good any surfaces disturbed, and reinstatement of the circuit to its original, correctly protected configuration for 2-4mm

	4.3
	Remove Temporary Cabling & Reinstate Proper Connection 6-10 mm
	Remove the temporary electrical cable extension installed, and reinstate a proper, code-compliant permanent connection/isolation as per the original design. Work to include: safe isolation and removal of the temporary cabling, making good any surfaces disturbed, and reinstatement of the circuit to its original, correctly protected configuration for 5 to 10mm.

	4.4
	Remove Temporary Cabling & Reinstate Proper Connection 10 25 mm
	Remove the temporary electrical cable extension installed and reinstate a proper, code-compliant permanent connection/isolation as per the original design. Work to include: safe isolation and removal of the temporary cabling, making good any surfaces disturbed, and reinstatement of the circuit to its original, correctly protected configuration for 10 -25 mm.

	4.5
	Fixing and Repairing - General Cables, Wires, Panels
	Check and repair all existing cables, wires, sockets, outlets, electrical panel boards and circuit breakers, then prepare the suitable location to reinstall. Work to include: visual and continuity testing of accessible circuits, repair or replacement of damaged cabling/accessories, and confirmation of correct, safe operation prior to closing up.

	4.6
	Control panels for submersible pumps
	Replace flooded control panel for submersible pumps same as existing including all necessary works and accessories

	4.7
	Disconnecting Switches - 4x63A 4-Pole Waterproof (Basement)
	Supply and install new disconnecting switch, 4 x 63A, 4-pole, waterproof-rated, located in the basement, similar to existing. Work to include: removal of the failed unit, fixing and wiring of the new switch, and testing of isolation function.

	4.8
	Disconnecting Switches - 4x40A 4-Pole Waterproof (Basement)
	Supply and install new disconnecting switch, 4 x 40A, 4-pole, waterproof-rated, located in the basement, similar to existing. Work to include: removal of the failed unit, fixing and wiring of the new switch, and testing of isolation function.

	4.9
	Electrical Sockets - 16A Simplex 2P+E
	Supply and install new 16 Amp Simplex Socket, 2P+E, similar to existing, complete with back box, wiring to the nearest suitable point, and cover plate.

	4.10
	Electrical Sockets - 16A Simplex Waterproof
	Supply and install new 16 Amp Simplex Socket, waterproof-rated, similar to existing, complete with back box, wiring to the nearest suitable point, and weatherproof cover.

	4.11
	Electrical Sockets - 16A Simplex UPS Socket
	Supply and install new 16 Amp Simplex UPS socket, 2P+E, similar to existing, complete with back box, dedicated wiring to the UPS distribution circuit, and cover plate.

	4.12
	Switches - 10A One Way One Gang
	Supply and install new 10 AMP switch, one way, one gang, similar to existing, complete with back box, wiring and cover plate.

	4.13
	Switches - 10A One Way Two Gangs
	Supply and install new 10 AMP switch, one way, two gangs, similar to existing, complete with back box, wiring and cover plate.

	4.14
	Switches - 10A Two Ways One Gang
	Supply and install new 10 AMP switch, two ways, one gang, similar to existing, complete with back box, wiring and cover plate.

	4.15
	Switches - 10A Two Ways Two Gangs
	Supply and install new 10 AMP switch, two ways, two gangs, similar to existing, complete with back box, wiring and cover plate.

	4.16
	Staircase Light Push-Button (Minuterie)
	Supply and install new 10 AMP staircase light push-button switch for minuterie control, similar to existing, complete with back box, wiring and cover plate, and tested for correct timed operation.

	4.17
	Lighting Fixtures - TYPE B Twin T8 LED (Replace Complete)
	Supply and install TYPE B lighting fixture, replacing the complete existing fixture with new: Twin T8 LED tube, surface-mount luminaire for interior use, 120cm, 40W - 4000K - 4700Lm, polycarbonate light grey colour, injected polyurethane double gasket, cover in clear UV-stabilised polycarbonate, cosφ ≥ 0.9. Work to include: removal and disposal of the existing fixture, fixing and wiring of the new fixture, and testing of correct illumination.

	4.18
	Lighting Fixtures - TYPE B Tube Replacement Only
	Supply and replace only the T8 tubes in existing TYPE B lighting fixtures, similar to existing specification, complete with testing of correct illumination on completion.

	4.19
	Lighting Fixtures - TYPE A 120cm LED Panel (Classroom)
	Supply and install TYPE A 120 cm LED panel for classrooms, similar to existing. Work to include: removal and disposal of the existing fixture, fixing and wiring of the new panel, and testing of correct illumination.

	4.20
	Lighting Fixtures - TYPE A1 LED Panel (Corridor)
	Supply and install TYPE A1 LED panel, 3600lm - 33W - 4000K - 80CRI, surface-mount/recessed, die-cast aluminum, IP20, 600 x 600mm, for corridors. Work to include: removal and disposal of the existing fixture, fixing and wiring of the new panel, and testing of correct illumination.

	4.21
	Lighting Fixtures - TYPE H Round Spot (Ground Floor)
	Supply and install TYPE H round spot with E27 holder, for the Ground Floor, similar to existing. Work to include: removal and disposal of the existing fixture, fixing and wiring of the new fixture, and testing.

	4.22
	Lighting Fixtures - E27 LED 14W
	Supply and install LED light, E27 fitting, 14W, similar to existing. Work to include: removal and disposal of the existing lamp/fixture as applicable, fixing and wiring, and testing of correct illumination.

	4.23
	Lighting Fixtures - TYPE CC Twin T8 LED (WC)
	Supply and install TYPE CC Twin T8 LED tube, recessed-mounted luminaire, for WC areas, similar to existing. Work to include: removal and disposal of the existing fixture, fixing and wiring of the new fixture, and testing of correct illumination.

	4.24
	Lighting Fixtures - TYPE M Motion-Sensor LED
	Supply and install TYPE M LED fixture, 1500lm - 17W - 4000K - 80CRI, ceiling-mounted, with integral motion sensor, similar to existing. Work to include: removal and disposal of the existing fixture, fixing and wiring of the new fixture, and testing of sensor operation and illumination.

	4.25
	Lighting Fixtures - Emergency (Replace Existing EM)
	Supply and install new LED emergency light fixture to replace each existing emergency (EM) fixture. Work to include: removal and disposal of the existing unit, fixing and wiring of the new fixture on the emergency circuit, and testing of battery back-up operation.

	4.26
	Lighting Fixtures - Exit Signs (Replace Existing)
	Supply and install new LED exit sign to replace each existing exit sign. Work to include: removal and disposal of the existing unit, fixing and wiring of the new sign on the emergency circuit, and testing of illumination and battery back-up operation.

	4.27
	Test UPS System (No Replacement)
	Test the existing Uninterruptible Power Supply (UPS 10 KVA) system to confirm it is functioning correctly and operating within acceptable parameters. Work to include: functional testing under load, battery-backup duration check, and a written report of findings and any deficiencies to the LRC Engineer. Battery replacement is excluded from this item.

	4.28
	Replace Damaged Photovoltaic Panels (600W)
	Remove damaged/broken 600W multi-crystalline photovoltaic panels and supply, install and reconnect new panels matching existing specification. Work to include: safe isolation of the affected string, removal and disposal of damaged panels, fixing of new panels to the existing mounting structure, re-wiring, and testing of the affected string(s) for correct output. Quantity per the original Ministry design's surveyed count of damaged panels.

	4.29
	Parking Management System - Test Only (No Repair)
	Test the electrical and control wiring for the car-parking management system (automatic barriers/gates, car-counting system, card readers) once power supply is confirmed. Work to include: functional testing of each component, and a written report of any faults found to the LRC Engineer. Repair works are excluded from this item and, if required, will be scoped separately.

	4.30
	Earthing System - Testing
	Test the earthing system to confirm perfect operating condition, including the earth pits, earth test links, earth bars, and earth continuity conduits to all panels and motors. of all low-current systems as per specifications, with a written test report on completion.

	4.31
	Lightning Protection System
	Rehabilitate and test the complete lightning protection system to ensure safety, comprising a Franklin rod at roof level with copper stranded bare conductor (3 x 25 mm) and all accessories and connections to the ground earth network. Work to include: inspection and repair of the air terminal, down-conductors and earth connections, continuity testing, and a written test report on completion.

	4.32
	Distribution Boards - Testing & Certification Final Testing & Handover Certification
	Carry out general testing and certification of low-voltage distribution boards throughout the building. Work to include: visual inspection, insulation resistance and continuity testing, verification of correct labelling, and issue of a test certificate for each board. And  Carry out final testing and certification of all repaired/reconnected circuits and systems prior to handover. Work to include: functional testing of each system, compilation of test results, and preparation of as-built documentation for the LRC Engineer.
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