## Annex 2 – Bid Form completed signed and stamped

- All bids must be typed; handwritten bids will not be considered.

- The contract will be awarded to the lowest-cost technically compliant complete lots

- The quantities mentioned below are required unless there is a variation within a specified range with proper justification. The LRC reserves the right to increase or decrease the quantities.

- The bidder is not permitted to alter the section labelled “LRC to complete” below. Bidder is not allowed to use any other template.

- In the event of any discrepancy between the unit price and the total price, LRC reserves the right to rely on the unit price as stated in the financial bid, rather than the total price without go back to the supplier. The unit price must be provided with no more than two decimal places.

- Bids must include transportation, insurance, installation, commissioning or other charges. No additional charges shall be accepted unless expressly agreed by LRC in writing.

Lot 1: SITE WORKS

| LRC to Complete (BIDDERS ARE NOTE ALLOWED TO MODIFY THE LRC SECTION) |  | BIDDER to Complete |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Item Number | Item/Milestone Required | Unit of Measurement | Estimated Quantity | Unit Price in USD, Exclusive VAT | VAT (%) | Unit Price in USD, inclusive VAT | Total Price in USD, inclusive VAT | Lead time of Delivery from the date of the purchase order |
| 1.1 | Demolition of redundant structures, and obstructions | m³ | 100 |  |  |  |  |  |
| 1.2 | Dismantling, set-aside & reinstatement of existing tanks, equipment and obstructions to clear the area | No. | 5 |  |  |  |  |  |
| 1.3 | Excavation in any material for foundations, trenches and equipment bases | m³ | 120 |  |  |  |  |  |
| 1.4 | Backfilling & compaction with approved material | m³ | 90 |  |  |  |  |  |
| 1.5 | Asphalt cutting, pavement removal and reinstatement over cable and pipe routes | m² | 85 |  |  |  |  |  |
| 1.6 | New asphalt pavement — subbase + base course + wearing course | m² | 100 |  |  |  |  |  |
| 1.7 | Granular subbase material — supply, spread and compact | m² | 450 |  |  |  |  |  |
| 1.8 | Precast concrete kerbstone — supply and lay on concrete bed | m | 165 |  |  |  |  |  |

Lot 2: CIVIL & STRUCTURAL WORKS

| LRC to Complete (BIDDERS ARE NOTE ALLOWED TO MODIFY THE LRC SECTION) |  | BIDDER to Complete |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Item Number | Item/Milestone Required | Unit of Measurement | Estimated Quantity | Unit Price in USD, Exclusive VAT | VAT (%) | Unit Price in USD, inclusive VAT | Total Price in USD, inclusive VAT | Lead time of Delivery from the date of the purchase order |
| 2.1 | Reinforced concrete, C25/30 — measured per cubic metre (foundations, plinths, ballast blocks, bases) | m³ | 500 |  |  |  |  |  |
| 2.2 | Concrete block wall, 15 cm thick — to equipment rooms, compounds and enclosures | m² | 300 |  |  |  |  |  |
| 2.3 | Concrete block wall, 20 cm thick — to equipment rooms, compounds and enclosures | m² | 300 |  |  |  |  |  |
| 2.4 | Internal & external plastering | m² | 400 |  |  |  |  |  |
| 2.5 | Internal & external painting — with putty | m² | 170 |  |  |  |  |  |
| 2.6 | Internal & external painting — without putty | m² | 265 |  |  |  |  |  |
| 2.7 | External stone cladding (local stone) — stone type as instructed by the Engineer or matching existing | m² | 10 |  |  |  |  |  |
| 2.8 | Floor tiling (European-made) — tile type, size and colour as instructed by the Engineer or matching existing | m² | 51 |  |  |  |  |  |
| 2.9 | Wall tiling (European-made) — tile type, size and colour as instructed by the Engineer or matching existing | m² | 34 |  |  |  |  |  |
| 2.10 | Reinforced concrete electrical manhole / cable draw-pit — Extra-small, 40 × 40 × 50 cm internal, with medium-duty (B125) cover | No. | 14 |  |  |  |  |  |
| 2.11 | Reinforced concrete electrical manhole / cable draw-pit — Small, 60 × 60 × 60 cm internal, with medium-duty (C250) cover | No. | 15 |  |  |  |  |  |
| 2.12 | Reinforced concrete electrical manhole / cable draw-pit — Large, 100 × 100 × 120 cm internal, with medium-duty (D400) cover | No. | 4 |  |  |  |  |  |
| 2.13 | Polyurethane (PU) liquid waterproofing membrane — reinstatement at roof penetrations and PV fixings | m² | 240 |  |  |  |  |  |
| 2.14 | APP / SBS torch-applied bituminous membrane — roof waterproofing | m² | 150 |  |  |  |  |  |
| 2.15 | Core drilling of wall / slab for cable and conduit penetration, with sealing and making good | No. | 50 |  |  |  |  |  |
| 2.16 | Rainwater downpipe (uPVC) 2" (DN50) & brackets — reinstatement / diversion around PV works | m | 65 |  |  |  |  |  |
| 2.17 | Rainwater downpipe (uPVC) 4" (DN100) & brackets — reinstatement / diversion around PV works | m | 55 |  |  |  |  |  |
| 2.18 | U-shaped drainage channel at array and equipment-compound edge | m | 80 |  |  |  |  |  |
| 2.19 | Chain-link security fence, 2.0 m high, to ground-mounted array or equipment compound | m | 250 |  |  |  |  |  |
| 2.20 | Pedestrian gate 1.0 × 2.0 m to match fence | No. | 5 |  |  |  |  |  |
| 2.21 | Fixed steel bollard (ø100 mm, 900 mm above ground) — protection to equipment and cable risers | No. | 15 |  |  |  |  |  |

Lot 3: PV MODULES, MOUNTING STRUCTURES & EQUIPMENT HOUSING

| LRC to Complete (BIDDERS ARE NOTE ALLOWED TO MODIFY THE LRC SECTION) |  | BIDDER to Complete |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Item Number | Item/Milestone Required | Unit of Measurement | Estimated Quantity | Unit Price in USD, Exclusive VAT | VAT (%) | Unit Price in USD, inclusive VAT | Total Price in USD, inclusive VAT | Lead time of Delivery from the date of the purchase order |
| 3.1 | PV module — supply & install complete with module-level balance of system (per Wp) | Wp | 490000 |  |  |  |  |  |
| 3.2 | PV module — replace existing module in an operating array (per Wp) | Wp | 20000 |  |  |  |  |  |
| 3.3 | PV mounting structure — flat or pitched roof (per module) — 2.7 mm min. member thickness | No. | 200 |  |  |  |  |  |
| 3.4 | PV mounting structure — ground mounted on concrete bases or curbstone (per module) — 2.7 mm min. member thickness | No. | 500 |  |  |  |  |  |
| 3.5 | Elevated PV support structure (raised canopy / carport type) over usable ground — 2.7 mm min. steel section thickness | No. | 500 |  |  |  |  |  |
| 3.6 | Elevated PV support structure (raised canopy / carport type) over usable ground — 5 mm min. steel section thickness | No. | 50 |  |  |  |  |  |
| 3.7 | Sandwich panel 5 cm with supporting steel structure — roof / wall to equipment enclosure | m² | 45 |  |  |  |  |  |
| 3.8 | Sandwich panel 10 cm with supporting steel structure — roof / wall to equipment enclosure | m² | 40 |  |  |  |  |  |
| 3.9 | External steel door (approx. 0.90 × 2.10 m) to inverter / battery / pump room | No. | 6 |  |  |  |  |  |
| 3.10 | Steel pole 4 m — for solar luminaire, PV panel or overhead cable support | No. | 20 |  |  |  |  |  |
| 3.11 | Steel pole 6 m — for solar luminaire, PV panel or overhead cable support | No. | 15 |  |  |  |  |  |
| 3.12 | Solar LED street lamp 30 W (split type, separate PV panel) | No. | 20 |  |  |  |  |  |
| 3.13 | Solar LED street lamp 50 W (split type, separate PV panel) | No. | 15 |  |  |  |  |  |

Lot 4: INVERTERS, ENERGY STORAGE & REMOVAL OF REDUNDANT EQUIPMENT

| LRC to Complete (BIDDERS ARE NOTE ALLOWED TO MODIFY THE LRC SECTION) |  | BIDDER to Complete |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Item Number | Item/Milestone Required | Unit of Measurement | Estimated Quantity | Unit Price in USD, Exclusive VAT | VAT (%) | Unit Price in USD, inclusive VAT | Total Price in USD, inclusive VAT | Lead time of Delivery from the date of the purchase order |
| 4.1 | Hybrid inverter 3 kW — single-phase (incl. AC/DC protection panel & accessories, and removal of existing inverter where present) | No. | 2 |  |  |  |  |  |
| 4.2 | Hybrid inverter 5 kW — single-phase (incl. AC/DC protection panel & accessories, and removal of existing inverter where present) | No. | 2 |  |  |  |  |  |
| 4.3 | Hybrid inverter 8 kW — single-phase (incl. AC/DC protection panel & accessories, and removal of existing inverter where present) | No. | 4 |  |  |  |  |  |
| 4.4 | Hybrid inverter 10 kW — single-phase (incl. AC/DC protection panel & accessories, and removal of existing inverter where present) | No. | 3 |  |  |  |  |  |
| 4.5 | Hybrid inverter 12 kW — single-phase (incl. AC/DC protection panel & accessories, and removal of existing inverter where present) | No. | 2 |  |  |  |  |  |
| 4.6 | Hybrid inverter 16 kW — single-phase (incl. AC/DC protection panel & accessories, and removal of existing inverter where present) | No. | 2 |  |  |  |  |  |
| 4.7 | Hybrid inverter 5 kW — THREE-PHASE (incl. AC/DC protection panel & accessories, and removal of existing inverter where present) | No. | 2 |  |  |  |  |  |
| 4.8 | Hybrid inverter 8 kW — THREE-PHASE (incl. AC/DC protection panel & accessories, and removal of existing inverter where present) | No. | 2 |  |  |  |  |  |
| 4.90 | Hybrid inverter 10 kW — THREE-PHASE (incl. AC/DC protection panel & accessories, and removal of existing inverter where present) | No. | 2 |  |  |  |  |  |
| 4.10 | Hybrid inverter 12 kW — THREE-PHASE (incl. AC/DC protection panel & accessories, and removal of existing inverter where present) | No. | 4 |  |  |  |  |  |
| 4.11 | Hybrid inverter 16 kW — THREE-PHASE (incl. AC/DC protection panel & accessories, and removal of existing inverter where present) | No. | 3 |  |  |  |  |  |
| 4.12 | Hybrid inverter 20 kW — THREE-PHASE (incl. AC/DC protection panel & accessories, and removal of existing inverter where present) | No. | 2 |  |  |  |  |  |
| 4.13 | Hybrid inverter 15 kW — HIGH-VOLTAGE battery type (incl. AC/DC protection panel & accessories, and removal of existing inverter where present) | No. | 1 |  |  |  |  |  |
| 4.14 | Hybrid inverter 20 kW — HIGH-VOLTAGE battery type (incl. AC/DC protection panel & accessories, and removal of existing inverter where present) | No. | 1 |  |  |  |  |  |
| 4.15 | Hybrid inverter 25 kW — HIGH-VOLTAGE battery type (incl. AC/DC protection panel & accessories, and removal of existing inverter where present) | No. | 1 |  |  |  |  |  |
| 4.16 | Hybrid inverter 30 kW — HIGH-VOLTAGE battery type (incl. AC/DC protection panel & accessories, and removal of existing inverter where present) | No. | 1 |  |  |  |  |  |
| 4.17 | Hybrid inverter 40 kW — HIGH-VOLTAGE battery type (incl. AC/DC protection panel & accessories, and removal of existing inverter where present) | No. | 1 |  |  |  |  |  |
| 4.18 | Hybrid inverter 50 kW — HIGH-VOLTAGE battery type (incl. AC/DC protection panel & accessories, and removal of existing inverter where present) | No. | 2 |  |  |  |  |  |
| 4.19 | Hybrid inverter 60 kW — HIGH-VOLTAGE battery type (incl. AC/DC protection panel & accessories, and removal of existing inverter where present) | No. | 1 |  |  |  |  |  |
| 4.20 | Hybrid inverter 80 kW — HIGH-VOLTAGE battery type (incl. AC/DC protection panel & accessories, and removal of existing inverter where present) | No. | 1 |  |  |  |  |  |
| 4.21 | Lithium battery 48–52 V 100 Ah (LFP with integral BMS) | No. | 6 |  |  |  |  |  |
| 4.22 | Lithium battery 48–52 V 200 Ah (LFP with integral BMS) | No. | 3 |  |  |  |  |  |
| 4.23 | Lithium battery 48–52 V 300 Ah (LFP with integral BMS) | No. | 2 |  |  |  |  |  |
| 4.24 | Rack-mounted lithium battery 48–52 V 100 Ah (LFP with integral BMS) | No. | 30 |  |  |  |  |  |
| 4.25 | HIGH-VOLTAGE lithium battery module (LFP, stackable, >200 V DC nominal) — per kWh | kWh | 200 |  |  |  |  |  |
| 4.26 | HIGH-VOLTAGE battery base / master control unit with high-voltage box | No. | 4 |  |  |  |  |  |

Lot 5: ELECTRICAL WORKS, CONTAINMENT, PROTECTION & DISTRIBUTION

| LRC to Complete (BIDDERS ARE NOTE ALLOWED TO MODIFY THE LRC SECTION) |  | BIDDER to Complete |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Item Number | Item/Milestone Required | Unit of Measurement | Estimated Quantity | Unit Price in USD, Exclusive VAT | VAT (%) | Unit Price in USD, inclusive VAT | Total Price in USD, inclusive VAT | Lead time of Delivery from the date of the purchase order |
| 5.1 | DC combiner box (IP54/IP65, fused, with string monitoring provision) | No. | 100 |  |  |  |  |  |
| 5.2 | AC/DC protection enclosure with surge protective devices (SPDs) | No. | 20 |  |  |  |  |  |
| 5.3 | Inverter protection enclosure (IP54/IP65) — AC and DC isolation local to the inverter | No. | 20 |  |  |  |  |  |
| 5.4 | Monitoring, control & remote data-logging — complete per system | No. | 15 |  |  |  |  |  |
| 5.5 | Earthing system for a solar installation — electrodes, conductors & bonding (≤5 Ω) | No. | 15 |  |  |  |  |  |
| 5.6 | Lightning protection system for a solar installation (structures up to 4 floors) | No. | 10 |  |  |  |  |  |
| 5.7 | Change-over / transfer switch — manual (MTS) AND automatic (ATS), single- or three-phase, up to 4 × 400 A, in IP54 panel (EDL / generator / solar) | No. | 13 |  |  |  |  |  |
| 5.8 | Main distribution board (12–24 way, populated, all devices double-pole) | No. | 6 |  |  |  |  |  |
| 5.9 | Circuit breaker box (6-way, double-pole devices) | No. | 17 |  |  |  |  |  |
| 5.10 | Contactor — four-pole (3P+N), 40 A (AC-1), 230 V AC coil, with auxiliary contacts | No. | 6 |  |  |  |  |  |
| 5.11 | Copper wiring circuit 1.5 mm² — concealed conduit (final circuits) | m | 193 |  |  |  |  |  |
| 5.12 | Copper wiring circuit 2.5 mm² — concealed conduit (final circuits) | m | 203 |  |  |  |  |  |
| 5.13 | Copper wiring circuit 4 mm² — concealed conduit (final circuits) | m | 104 |  |  |  |  |  |
| 5.14 | Copper wiring circuit 6 mm² — concealed conduit (final circuits) | m | 60 |  |  |  |  |  |
| 5.15 | Copper wiring circuit 1.5 mm² — surface conduit / trunking (final circuits) | m | 282 |  |  |  |  |  |
| 5.16 | Copper wiring circuit 2.5 mm² — surface conduit / trunking (final circuits) | m | 312 |  |  |  |  |  |
| 5.17 | Copper wiring circuit 4 mm² — surface conduit / trunking (final circuits) | m | 176 |  |  |  |  |  |
| 5.18 | Copper wiring circuit 6 mm² — surface conduit / trunking (final circuits) | m | 110 |  |  |  |  |  |
| 5.19 | Galvanised perforated cable tray 100 mm wide with covers, supports & earth continuity | m | 260 |  |  |  |  |  |
| 5.20 | Galvanised perforated cable tray 200 mm wide with covers, supports & earth continuity | m | 130 |  |  |  |  |  |
| 5.21 | Galvanised perforated cable tray 300 mm wide with covers, supports & earth continuity | m | 60 |  |  |  |  |  |
| 5.22 | Cable trench 0.60 × 0.40 m — complete: excavate, sand-bed, duct, warning tape, backfill & reinstate | m | 100 |  |  |  |  |  |
| 5.23 | Power socket outlet 10 A — supply, install & connect | No. | 30 |  |  |  |  |  |
| 5.24 | Power socket outlet 16 A — supply, install & connect (dedicated circuit) | No. | 10 |  |  |  |  |  |
| 5.25 | Power / lighting switch — 1-way, 2-way or intermediate, single or multi-gang | No. | 30 |  |  |  |  |  |
| 5.26 | Exhaust / extract fan — general purpose | No. | 10 |  |  |  |  |  |
| 5.27 | Lighting point — concealed conduit (LED 40 W) | No. | 30 |  |  |  |  |  |
| 5.28 | Lighting point — surface / external (LED 40 W, IP65) | No. | 35 |  |  |  |  |  |
| 5.29 | Illuminated exit sign (running-man, LED, battery-backed ≥3 h) | No. | 10 |  |  |  |  |  |
| 5.30 | Smoke / heat detector with sounder | No. | 10 |  |  |  |  |  |
| 5.31 | Power, control & protection devices — circuit breakers, contactors, SPDs, protection & control relays | No. | 13 |  |  |  |  |  |

Lot 6: SOLAR WATER PUMPING SYSTEMS

| LRC to Complete (BIDDERS ARE NOTE ALLOWED TO MODIFY THE LRC SECTION) |  | BIDDER to Complete |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Item Number | Item/Milestone Required | Unit of Measurement | Estimated Quantity | Unit Price in USD, Exclusive VAT | VAT (%) | Unit Price in USD, inclusive VAT | Total Price in USD, inclusive VAT | Lead time of Delivery from the date of the purchase order |
| 6.1 | Electric panel for solar pumping VFD + sinewave filter (IP54) | No. | 2 |  |  |  |  |  |
| 6.2 | Solar pumping VFD drive 2 HP | No. | 1 |  |  |  |  |  |
| 6.3 | Solar pumping VFD drive 5 HP | No. | 1 |  |  |  |  |  |
| 6.4 | Solar pumping VFD drive 7.5 HP | No. | 1 |  |  |  |  |  |
| 6.5 | Solar pumping VFD drive 10 HP | No. | 1 |  |  |  |  |  |
| 6.6 | Solar pumping VFD drive 15 HP | No. | 1 |  |  |  |  |  |
| 6.7 | Solar pumping VFD drive 20 HP | No. | 1 |  |  |  |  |  |
| 6.8 | Solar pumping VFD drive 25 HP | No. | 1 |  |  |  |  |  |
| 6.9 | Solar pumping VFD drive 30 HP | No. | 1 |  |  |  |  |  |
| 6.10 | Solar pumping VFD drive 40 HP | No. | 1 |  |  |  |  |  |
| 6.11 | Solar pumping VFD drive 50 HP | No. | 1 |  |  |  |  |  |
| 6.12 | Solar pumping VFD drive 60 HP | No. | 1 |  |  |  |  |  |
| 6.13 | Solar pumping VFD drive 70 HP | No. | 1 |  |  |  |  |  |
| 6.14 | Solar pumping VFD drive 80 HP | No. | 1 |  |  |  |  |  |
| 6.15 | Solar pumping VFD drive 90 HP | No. | 1 |  |  |  |  |  |
| 6.16 | Solar pumping VFD drive 100 HP | No. | 1 |  |  |  |  |  |
| 6.17 | Solar pumping VFD drive 125 HP | No. | 1 |  |  |  |  |  |
| 6.18 | Solar pumping VFD drive 150 HP | No. | 1 |  |  |  |  |  |
| 6.19 | Solar pumping VFD drive 180 HP | No. | 1 |  |  |  |  |  |
| 6.20 | Solar pumping VFD drive 200 HP | No. | 1 |  |  |  |  |  |
| 6.21 | Solar pumping VFD drive 250 HP | No. | 1 |  |  |  |  |  |
| 6.22 | Solar pumping VFD drive 300 HP | No. | 1 |  |  |  |  |  |
| 6.23 | Sinewave output filter — for VFD 2 HP | No. | 1 |  |  |  |  |  |
| 6.24 | Sinewave output filter — for VFD 5 HP | No. | 1 |  |  |  |  |  |
| 6.25 | Sinewave output filter — for VFD 7.5 HP | No. | 1 |  |  |  |  |  |
| 6.26 | Sinewave output filter — for VFD 10 HP | No. | 1 |  |  |  |  |  |
| 6.27 | Sinewave output filter — for VFD 15 HP | No. | 1 |  |  |  |  |  |
| 6.28 | Sinewave output filter — for VFD 20 HP | No. | 1 |  |  |  |  |  |
| 6.29 | Sinewave output filter — for VFD 25 HP | No. | 1 |  |  |  |  |  |
| 6.30 | Sinewave output filter — for VFD 30 HP | No. | 1 |  |  |  |  |  |
| 6.31 | Sinewave output filter — for VFD 40 HP | No. | 1 |  |  |  |  |  |
| 6.32 | Sinewave output filter — for VFD 50 HP | No. | 1 |  |  |  |  |  |
| 6.33 | Sinewave output filter — for VFD 60 HP | No. | 1 |  |  |  |  |  |
| 6.34 | Sinewave output filter — for VFD 70 HP | No. | 1 |  |  |  |  |  |
| 6.35 | Sinewave output filter — for VFD 80 HP | No. | 1 |  |  |  |  |  |
| 6.36 | Sinewave output filter — for VFD 90 HP | No. | 1 |  |  |  |  |  |
| 6.37 | Sinewave output filter — for VFD 100 HP | No. | 1 |  |  |  |  |  |
| 6.38 | Sinewave output filter — for VFD 125 HP | No. | 1 |  |  |  |  |  |
| 6.39 | Sinewave output filter — for VFD 150 HP | No. | 1 |  |  |  |  |  |
| 6.40 | Sinewave output filter — for VFD 180 HP | No. | 1 |  |  |  |  |  |
| 6.41 | Sinewave output filter — for VFD 200 HP | No. | 1 |  |  |  |  |  |
| 6.42 | Sinewave output filter — for VFD 250 HP | No. | 1 |  |  |  |  |  |
| 6.43 | Sinewave output filter — for VFD 300 HP | No. | 1 |  |  |  |  |  |
| 6.44 | Additional cable run beyond the first 50 m (array to pump / panel) | m | 200 |  |  |  |  |  |
| 6.45 | Pump control panel with float / pressure switch & tank level control | No. | 2 |  |  |  |  |  |
| 6.46 | Borehole water level monitoring & dry-run protection — submersible level sensor with sounding pipe | No. | 2 |  |  |  |  |  |

Lot 7: ENGINEERING DOCUMENTATION & HANDOVER

| LRC to Complete (BIDDERS ARE NOTE ALLOWED TO MODIFY THE LRC SECTION) |  | BIDDER to Complete |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Item Number | Item/Milestone Required | Unit of Measurement | Estimated Quantity | Unit Price in USD, Exclusive VAT | VAT (%) | Unit Price in USD, inclusive VAT | Total Price in USD, inclusive VAT | Lead time of Delivery from the date of the purchase order |
| 7.1 | Engineering design, calculations & shop drawings for a solar installation (pre-construction) (2 hard copies + soft copy on USB and by email ) | No. | 15 |  |  |  |  |  |
| 7.2 | As-built drawings of the completed solar installation (AutoCAD + PDF) (2 hard copies + soft copy on USB and by email) | No. | 15 |  |  |  |  |  |
| 7.3 | O&M manual (2 hard copies + soft copy on USB and by email) & warranty certificates | Set | 15 |  |  |  |  |  |

Lot 8: DAYWORKS

| LRC to Complete (BIDDERS ARE NOTE ALLOWED TO MODIFY THE LRC SECTION) |  | BIDDER to Complete |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Item Number | Item/Milestone Required | Unit of Measurement | Estimated Quantity | Unit Price in USD, Exclusive VAT | VAT (%) | Unit Price in USD, inclusive VAT | Total Price in USD, inclusive VAT | Lead time of Delivery from the date of the purchase order |
| 8.1 | Dayworks — solar / electrical technician (per man-day, 8 hours) | day | 20 |  |  |  |  |  |

## ANNEX 3: DETAILED SPECIFICATIONS

|  | Item Code | Item / Title | Standard | Description (English) | Type | Unit |
| --- | --- | --- | --- | --- | --- | --- |
|  | SOL-1 SITE WORKS |  |  |  |  |  |
| 1.1 | SOL-1.01 | Demolition of redundant structures, and obstructions | — | Demolish, remove, and dispose of redundant structures, other permanent obstructions within the solar installation area, only on the Engineer's prior written instruction and against an agreed scope statement. The works include confirming the limits of demolition; locating, isolating and protecting existing services. Measured per m3 of demolition waste for the instructed scope. | Service | m³ |
| 1.2 | SOL-1.02 | Dismantling, set-aside & reinstatement of existing tanks, equipment and obstructions to clear the area | — | Temporarily remove and reinstate existing water tanks, equipment, pipework, supports, cabling and other reusable obstructions within the solar installation area, only on the Engineer's prior written instruction and against an agreed scope statement. The works include safe isolation; draining where applicable; disconnection and careful dismantling; identification and recording of components and connections; lifting, handling, secure set-aside storage and protection throughout the works; preparation of the original or agreed new position; reinstallation complete with supports, anchors and all pipework, valves, fittings and electrical/control connections; refilling, leak testing, functional testing and return to service; and making good all disturbed finishes. Measured as a lump sum for the instructed scope. | Service | No. |
| 1.3 | SOL-1.03 | Excavation in any material for foundations, trenches and equipment bases | — | Excavate in any material, including soft rock and existing made ground, for PV array foundations, ballast pads, equipment room bases, earthing pits, manholes and cable trenches, to the lines, levels and depths shown or instructed. The works include setting out, trial holes to locate existing services, all necessary temporary support, planking, strutting and shoring of excavation faces, dewatering and keeping the excavation free of water, trimming and compaction of the formation, temporary protection and barriers around open excavations, and the loading, haulage and disposal off site of all surplus excavated material. Measured per cubic metre net in place from existing ground level. | Service | m³ |
| 1.4 | SOL-1.04 | Backfilling & compaction with approved material | — | Supply, place and compact approved backfill material around foundations, equipment bases and in trenches, in layers not exceeding 200 mm loose thickness, each layer watered and mechanically compacted to not less than 95% of the modified Proctor maximum dry density. The works include selected granular material where the excavated material is unsuitable, testing of compaction where required by the Engineer, and reinstatement of the surface to match the adjacent finish. Measured per cubic metre compacted in place. | Supply & Install | m³ |
| 1.5 | SOL-1.05 | Asphalt cutting, pavement removal and reinstatement over cable and pipe routes | — | Saw-cut the existing asphalt or concrete pavement to a straight neat line along a cable or pipe route, break out and remove the pavement and its base, and after the buried works are complete and approved reinstate the pavement to match the existing construction, including the compacted granular sub-base, bituminous base course, tack coat and wearing course, or concrete to the matching grade and finish, sealing of all joints with hot bitumen, reinstatement of any road markings removed, and the loading, haulage and disposal off site of all broken-out material. Measured per square metre of pavement cut, removed and reinstated. | Supply & Install | m² |
| 1.6 | SOL-1.06 | New asphalt pavement — subbase + base course + wearing course | — | Construct new asphalt pavement for an access road, equipment compound or hardstanding serving a solar installation, comprising a compacted granular sub-base, a bituminous base course and a bituminous wearing course laid to the specified thickness, levels and falls, including prime and tack coats, edge compaction, rolling to the specified density and all joints. Measured per square metre of completed pavement. with 5 cm thickness after compaction | Supply & Install | m² |
| 1.7 | SOL-1.07 | Granular subbase material — supply, spread and compact | — | Supply, spread, water and compact approved granular sub-base material to the specified thickness and levels beneath equipment compounds, ground-mounted array areas and access tracks, compacted in layers to not less than 95% of the modified Proctor maximum dry density and trimmed to the required falls. Measured per square metre at the 150 mm thickness. | Supply & Install | m² |
| 1.8 | SOL-1.08 | Precast concrete kerbstone — supply and lay on concrete bed | — | Supply and lay precast concrete kerbstone to define the edge of an equipment compound, access road or ground-mounted array area, bedded and haunched on a plain concrete foundation, laid true to line and level with tight jointing and pointing in cement mortar, including all cutting, closers and radius units. Measured per linear metre laid. | Supply & Install | m |
|  | SOL-2 CIVIL & STRUCTURAL WORKS |  |  |  |  |  |
| 2.1 | SOL-2.01 | Reinforced concrete, C25/30 — measured per cubic metre (foundations, plinths, ballast blocks, bases) | EN 206 / EN 1992-1-1 / EN 13670 | Supply, place, compact, cure and hand over reinforced concrete of strength class C25/30 to EN 206 (characteristic cylinder / cube strength 25 / 30 MPa), measured by volume, for PV array foundations and pad footings, ballast blocks, inverter and battery room bases, generator and equipment plinths, pump-house slabs, manhole surrounds and cable-trench haunching. The concrete shall be designed for exposure class XC2 for elements in contact with soil and XC4 for exposed external elements (XS1 for sites within 1 km of the coast), with the maximum water/cement ratio and minimum cement content required by EN 206 for that class. The minimum nominal cover to reinforcement shall be 40 mm generally and 50 mm for surfaces in contact with soil or cast on blinding. The works include sulphate-resisting cement where in contact with soil, plywood or steel formwork to a fair-faced finish with all necessary falsework and propping, ribbed reinforcement bars cut, bent, fixed and lapped in accordance with the approved bar-bending schedule together with all spacers, chairs and tying wire, cast-in anchor bolts, base plates, sleeves and earthing conductors positioned to template, mechanical vibration, and curing and protection for not less than seven days. Design shall be to EN 1992-1-1 and execution to EN 13670. All materials and works shall comply with EN 206, EN 1992-1-1 and EN 13670 (latest editions). Measured per cubic metre net in place; reinforcement, formwork and cast-in items are deemed included. | Supply & Install | m³ |
| 2.2 | SOL-2.02 | Concrete block wall, 15 cm thick — to equipment rooms, compounds and enclosures | EN 771-3 | Supply and build a concrete block wall 15 cm thick to form an inverter or battery room, a pump house, an equipment compound wall or a security enclosure. The works include hollow concrete blocks laid in cement-sand mortar in stretcher bond to true line, level and plumb, all bed and perpend joints raked or struck as required to receive plaster, horizontal bed-joint reinforcement, tying to the structural frame, forming of all openings with reinforced concrete lintels, sills and jambs, temporary propping, provision of ventilation openings and cable and pipe sleeves built in as the work proceeds, and curing. All materials and works shall comply with EN 771-3 (latest editions). Measured per square metre of wall face, deducting openings over 0.5 m². | Supply & Install | m² |
| 2.3 | SOL-2.03 | Concrete block wall, 20 cm thick — to equipment rooms, compounds and enclosures | EN 771-3 | Supply and build a concrete block wall 20 cm thick to form an inverter or battery room, a pump house, an equipment compound wall or a security enclosure. The works include hollow concrete blocks laid in cement-sand mortar in stretcher bond to true line, level and plumb, all bed and perpend joints raked or struck as required to receive plaster, horizontal bed-joint reinforcement, tying to the structural frame, forming of all openings with reinforced concrete lintels, sills and jambs, temporary propping, provision of ventilation openings and cable and pipe sleeves built in as the work proceeds, and curing. All materials and works shall comply with EN 771-3 (latest editions). Measured per square metre of wall face, deducting openings over 0.5 m². | Supply & Install | m² |
| 2.4 | SOL-2.04 | Internal & external plastering | EN 998-1 | Supply and apply cement-sand plaster to the internal or external faces of block or concrete walls, comprising a spatterdash key coat, a levelling undercoat ruled to screeds and a finishing coat rendered smooth and true, including angle beads at all arrises, stop beads at all edges, galvanised mesh over all junctions of dissimilar materials and over chases, making good around cable and pipe penetrations, waterproofing additive to external faces, and curing. All materials and works shall comply with EN 998-1 (latest editions). Measured per square metre of plastered face. | Supply & Install | m² |
| 2.5 | SOL-2.05 | Internal & external painting — with putty | EN 13300 | Prepare and paint the internal or external plastered surfaces with putty, comprising surface preparation, the application of not less than two coats of approved wall putty (acrylic internally, cement-based weather-resistant externally) over the entire surface, each coat sanded smooth to a uniform, even finish ready for painting, a sealer or primer coat and not less than two finishing coats of washable emulsion internally or acrylic weather-resistant paint externally, in the colour approved by the Engineer, together with the protection of all adjacent finishes and equipment and the making good of all disturbed work. All materials and works shall comply with EN 13300 (latest editions). Measured per square metre of painted face, putty included. | Supply & Install | m² |
| 2.6 | SOL-2.06 | Internal & external painting — without putty | EN 13300 | Prepare and paint the internal or external plastered surfaces without putty, comprising surface preparation by cleaning and removal of dust, loose material and efflorescence, local filling and sanding of minor cracks and defects only (no full putty coat), a sealer or primer coat and not less than two finishing coats of washable emulsion internally or acrylic weather-resistant paint externally, in the colour approved by the Engineer, together with the protection of all adjacent finishes and equipment and the making good of all disturbed work. All materials and works shall comply with EN 13300 (latest editions). Measured per square metre of painted face. | Supply & Install | m² |
| 2.7 | SOL-2.07 | External stone cladding (local stone) — stone type as instructed by the Engineer or matching existing | EN 1469 | Supply and install external cladding in local (Lebanese) natural stone to walls, of the stone type, colour, size, thickness and finish instructed by the Engineer, or matching the existing stone cladding and installation method of the building where no instruction is given, subject to the Engineer's prior approval of samples. The works include preparation of the substrate, fixing of the stone to the wall with cement-sand mortar and galvanised or stainless-steel ties and anchors, or with a stainless-steel mechanical fixing system where required, laid true to line, level and plumb with uniform joints, all cutting, returns, corners, sills, copings and edge pieces, pointing of joints in matching coloured mortar, cleaning on completion, and protection until handover. All materials and works shall comply with EN 1469 (latest editions). Measured per square metre of finished cladding face, deducting openings over 0.5 m². | Supply & Install | m² |
| 2.8 | SOL-2.08 | Floor tiling (European-made) — tile type, size and colour as instructed by the Engineer or matching existing | EN 14411 / EN 12004 | Supply and install European-made porcelain floor tiles (manufactured in Europe, with certificate of origin submitted to the Engineer), internal or external, of the tile type, size, colour and finish instructed by the Engineer, or matching the existing floor tiling where no instruction is given, subject to the Engineer's prior approval of samples. The works include preparation of the substrate, a cement-sand screed or bedding where required, fixing with approved cement-based tile adhesive or cement-sand mortar laid true to line, level and falls with uniform joints and spacers, anti-slip grade tiles where instructed (external areas, wet areas and equipment rooms), all cutting, edge trims and threshold profiles, matching tiled skirting, movement and perimeter joints, grouting of joints in approved colour-matched grout, cleaning on completion, and protection until handover. All materials and works shall comply with EN 14411 and EN 12004 (latest editions). Measured per square metre of finished floor tiled surface, deducting openings over 0.5 m²; skirting deemed included. | Supply & Install | m² |
| 2.9 | SOL-2.09 | Wall tiling (European-made) — tile type, size and colour as instructed by the Engineer or matching existing | EN 14411 / EN 12004 | Supply and install European-made porcelain wall tiles (manufactured in Europe, with certificate of origin submitted to the Engineer), internal or external, of the tile type, size, colour and finish instructed by the Engineer, or matching the existing wall tiling where no instruction is given, subject to the Engineer's prior approval of samples. The works include preparation of the substrate (plastered or rendered surface, true and plumb), fixing with approved cement-based tile adhesive applied with a notched trowel, tiles laid true to line, level and plumb with uniform joints and spacers, all cutting around openings, cable and pipe penetrations, edge trims, external and internal corner profiles, movement joints, grouting of joints in approved colour-matched grout, cleaning on completion, and protection until handover. All materials and works shall comply with EN 14411 and EN 12004 (latest editions). Measured per square metre of finished wall tiled surface, deducting openings over 0.5 m². | Supply & Install | m² |
| 2.10 | SOL-2.10 | Reinforced concrete electrical manhole / cable draw-pit — Extra-small, 40 × 40 × 50 cm internal, with medium-duty (B125) cover | EN 476 / EN 124 (B125) | Construct, complete and hand over a reinforced concrete electrical manhole or cable draw-pit on a cable route, of 40 × 40 cm internal plan dimensions and 50 cm internal depth (extra-small size — for single-duct pull points and short branch connections, 1 duct), comprising excavation, a 10 cm lean concrete blinding, a 10 cm reinforced concrete base slab (25 MPa), 10 cm reinforced concrete walls, an internal cement plaster render finished smooth, a 10 cm reinforced concrete cover slab with a medium-duty (Class B125) ductile iron or galvanised steel frame and lockable lid of approximately 35 × 35 cm clear opening set flush with the finished surface, 110 mm uPVC cable entry ducts and sleeves sealed against water and vermin, galvanised cable brackets and a draw rope, a gravel-filled drainage hole in the base, the earthing of all metalwork, backfilling and reinstatement of the surrounding surface, and permanent identification marking. All materials and works shall comply with EN 476 and EN 124 (B125) (latest editions). Measured per manhole complete. | Supply & Install | No. |
| 2.11 | SOL-2.11 | Reinforced concrete electrical manhole / cable draw-pit — Small, 60 × 60 × 60 cm internal, with medium-duty (C250) cover | EN 476 / EN 124(C250) | Construct, complete and hand over a reinforced concrete electrical manhole or cable draw-pit on a cable route, of 60 × 60 cm internal plan dimensions and 60 cm internal depth (small size — for short cable runs near inverters, PV arrays and distribution boards, up to 2 ducts), comprising excavation, a 10 cm lean concrete blinding, a 15 cm reinforced concrete base slab (25 MPa), 15 cm reinforced concrete walls or 20 cm concrete-filled block walls, an internal cement plaster render finished smooth, a 15 cm reinforced concrete cover slab with a medium-duty (Class C250) ductile iron or galvanised steel frame and lockable lid of approximately 50 × 50 cm clear opening set flush with the finished surface, 110 mm uPVC cable entry ducts and sleeves sealed against water and vermin, galvanised cable brackets and a draw rope, a sump of approximately 20 × 20 × 20 cm for drainage, the earthing of all metalwork, backfilling and reinstatement of the surrounding surface, and permanent identification marking. All materials and works shall comply with EN 476 and EN 124 (C250) (latest editions). Measured per manhole complete. | Supply & Install | No. |
| 2.12 | SOL-2.12 | Reinforced concrete electrical manhole / cable draw-pit — Large, 100 × 100 × 120 cm internal, with medium-duty (D400) cover | EN 476 / EN 124 (D400) | Construct, complete and hand over a reinforced concrete electrical manhole or cable draw-pit on a cable route, of 100 × 100 cm internal plan dimensions and 120 cm internal depth (large size — for cable junctions, changes of direction and routes with more than 4 ducts), comprising excavation, a 10 cm lean concrete blinding, a 20 cm reinforced concrete base slab (25 MPa), 20 cm reinforced concrete walls, an internal cement plaster render finished smooth, a 20 cm reinforced concrete cover slab with a medium-duty (Class D400) ductile iron or galvanised steel frame and lockable lid of approximately 80 × 80 cm clear opening set flush with the finished surface, 110 mm or 160 mm uPVC cable entry ducts and sleeves sealed against water and vermin, galvanised cable brackets and a draw rope, a sump of approximately 20 × 20 × 20 cm for drainage, the earthing of all metalwork, backfilling and reinstatement of the surrounding surface, and permanent identification marking. All materials and works shall comply with EN 476 and EN 124 (D400) (latest editions). Measured per manhole complete. | Supply & Install | No. |
| 2.13 | SOL-2.13 | Polyurethane (PU) liquid waterproofing membrane — reinstatement at roof penetrations and PV fixings | EAD 030350-00-0402 (formerly ETAG 005) | Supply and apply a UV-stable elastomeric polyurethane liquid waterproofing membrane to a roof or terrace surface disturbed by, or receiving, a PV mounting installation. The works include cleaning, drying and priming of the substrate, the forming of reinforced fillets at all upstands and penetrations, the local reinforcement of the membrane with polyester fleece at every anchor, bracket and cable penetration, the application of not less than two coats to the specified dry film thickness, water testing on completion, and a written waterproofing warranty. The membrane system shall hold a valid European Technical Assessment (ETA) issued against EAD 030350-00-0402 (formerly ETAG 005) for liquid-applied roof waterproofing kits, to be submitted to the Engineer for approval before use. All materials and works shall comply with EAD 030350-00-0402 (latest edition). Measured per square metre of membrane applied. | Supply & Install | m² |
| 2.14 | SOL-2.14 | APP / SBS torch-applied bituminous membrane — roof waterproofing | EN 13707 | Supply and lay a torch-applied APP or SBS modified bituminous waterproofing membrane on a prepared and primed roof substrate where the existing waterproofing has been removed or damaged by the solar installation. The works include a bituminous primer, the membrane fully bonded with not less than 100 mm side and 150 mm end laps sealed and rolled, reinforced upstands dressed not less than 150 mm above finished level and mechanically terminated, collars formed at all penetrations, a protection or separation layer where the membrane is overlaid, and water testing on completion. All materials and works shall comply with EN 13707 (latest editions). Measured per square metre laid. | Supply & Install | m² |
| 2.15 | SOL-2.15 | Core drilling of wall / slab for cable and conduit penetration, with sealing and making good | — | Form a clean circular penetration through a masonry or reinforced concrete wall or slab by diamond core drilling for the passage of cables, conduits or ducts, including a rebar scan prior to drilling to avoid cutting reinforcement, water control and collection, the sleeving of the opening, the sealing of the annulus with an approved fire-rated and weatherproof sealant, the fitting of internal and external cover plates or escutcheons, the making good of all disturbed finishes to match the existing, and the removal and disposal off site of all cores and arisings. Measured per core up to 200 mm diameter and 400 mm depth. | Service | No. |
| 2.16 | SOL-2.16 | Rainwater downpipe (uPVC) 2" (DN50) & brackets — reinstatement / diversion around PV works | EN 12200-1 | Supply and install a uPVC rainwater downpipe of 2" (DN50) nominal diameter with all bends, offsets, shoes, sockets and jointing, fixed to the structure with galvanised or stainless brackets at not more than 1.5 m centres, to reinstate or divert roof drainage disturbed by the PV mounting works and to discharge clear of the array, its foundations and all electrical equipment. All materials and works shall comply with EN 12200-1 (latest editions). Measured per linear metre installed. | Supply & Install | m |
| 2.17 | SOL-2.17 | Rainwater downpipe (uPVC) 4" (DN100) & brackets — reinstatement / diversion around PV works | EN 12200-1 | Supply and install a uPVC rainwater downpipe of 4" (DN100) nominal diameter with all bends, offsets, shoes, sockets and jointing, fixed to the structure with galvanised or stainless brackets at not more than 1.5 m centres, to reinstate or divert roof drainage disturbed by the PV mounting works and to discharge clear of the array, its foundations and all electrical equipment. All materials and works shall comply with EN 12200-1 (latest editions). Measured per linear metre installed. | Supply & Install | m |
| 2.18 | SOL-2.18 | U-shaped drainage channel at array and equipment-compound edge | EN 1433 | Supply and install a U-shaped surface drainage channel with a removable grating along the edge of a ground-mounted array, equipment compound or pump house, laid to falls on a concrete bed and haunching, complete with all connections to the existing drainage system, end caps, silt traps and access points. All materials and works shall comply with EN 1433 (latest editions). Measured per linear metre installed. | Supply & Install | m |
| 2.19 | SOL-2.19 | Chain-link security fence, 2.0 m high, to ground-mounted array or equipment compound | EN 10223 | Supply and erect a galvanised chain-link security fence not less than 2.0 m high around a ground-mounted PV array, battery enclosure or equipment compound, comprising galvanised steel line posts, straining posts each 2 m and struts set in concrete foundations 50 × 50 × 50, galvanised chain-link mesh opening of 5 cm or similar to existing, three lines of straining wire with tensioners, a barbed-wire or razor top where instructed, and the bonding of all metalwork to the site earthing system. All materials and works shall comply with EN 10223 (latest editions). Measured per linear metre of fence. | Supply & Install | m |
| 2.20 | SOL-2.20 | Pedestrian gate 1.0 × 2.0 m to match fence | — | Supply and install a galvanised steel pedestrian gate of approximately 1.0 × 2.0 m to match the adjoining fence, complete with a welded tubular frame and chain-link infill, heavy-duty hinges, a lockable latch and padlock hasp, a gate stop and drop bolt, concrete-set gate posts, the bonding of the gate and posts to the earthing system, and priming and finish painting. Measured per gate complete. | Supply & Install | No. |
| 2.21 | SOL-2.21 | Fixed steel bollard (ø100 mm, 900 mm above ground) — protection to equipment and cable risers | — | Supply and install a fixed steel bollard of 100 mm diameter standing 900 mm above finished ground level set in concrete foundations 50 × 50 × 50 to protect inverter cabinets, battery enclosures, cable risers and pump-house doors from vehicle impact, set in a concrete foundation, filled with concrete, capped, and primed and finished in high-visibility paint with reflective banding. Measured per bollard. | Supply & Install | No. |
|  | SOL-3 PV MODULES, MOUNTING STRUCTURES & EQUIPMENT HOUSING |  |  |  |  |  |
| 3.1 | SOL-3.01 | PV module — supply & install complete with module-level balance of system (per Wp) | IEC 61215 / IEC 61730 / IEC 62548 | Supply, transport, install, test and commission a high-efficiency monocrystalline photovoltaic module of the capacity stated in the call-off order, of not less than 22% module efficiency, with an IEC 61215 and IEC 61730 certified glass-front laminate, an anodised aluminium frame, an IP68 junction box with bypass diodes and MC4-compatible connectors, and a manufacturer's product warranty of not less than 12 years and a linear performance warranty of not less than 25 years. The works include the module-level balance of system: fixing the module to the mounting structure, earthing and bonding of the module frame, the MC4 connectors and module-to-module interconnections within the string, including SPDs, and combiner boxes, and the DC cable runs for all strings with the appropriate cross-section till the inverter. cable management and UV-resistant ties, permanent string and polarity labelling, string open-circuit voltage, short-circuit current, polarity and insulation testing, and including all labour, tools, access equipment, accessories, connectors, and incidental works required for a complete and fully operational installation. All materials and works shall comply with IEC 61215, IEC 61730 and IEC 62548 (latest editions). The mounting structure, rails, clamps and structural fixings are excluded from this item and are measured separately under SOL-3.03 to SOL-3.06. Measured per watt-peak of module nameplate capacity installed. | Supply & Install | Wp |
| 3.2 | SOL-3.02 | PV module — replace existing module in an operating array (per Wp) | IEC 61215 / IEC 61730 | Replace a defective or under-performing photovoltaic module in an existing operating array and disposal with a new module of matching or superior electrical characteristics. The works include the safe isolation and lock-out of the affected string, the disconnection and removal of the existing module, the inspection and, where required, the replacement of the associated MC4 connectors and cable tails, the fitting of the new module to the existing structure with all clamps and fixings, the re-establishment of frame earthing and bonding, string re-testing and comparison with the adjacent strings, the updating of the string record and labelling, and the delivery of the removed module to the end user or LRC store or to certified recycling as instructed by LRC engineer, including SPDs, and combiner boxes, and the DC cable runs for all strings with the appropriate cross-section till the inverter. All materials and works shall comply with IEC 61215 and IEC 61730 (latest editions). Measured per watt-peak of replacement module capacity installed. | Supply & Install | Wp |
| 3.3 | SOL-3.03 | PV mounting structure — flat or pitched roof (per module) — 2.7 mm min. member thickness | IEC 62548 / EN 1991-1-4 (wind) / EN ISO 1461 | Supply and install a hot-dip galvanised steel mounting structure, with all structural members (rails, legs, tilt frames and bracing) of not less than 2.7 mm material thickness, and all fixings to support one photovoltaic module on a flat roof, a tiled or sheeted pitched roof, including rails, mid and end clamps, roof hooks or ballast trays, adjustable tilt legs set to the design tilt and azimuth, MC4 cable pass-throughs, stainless-steel fasteners, and the earthing and bonding of rails and frames to the array earthing conductor. Module mid and end clamps may be of anodised aluminium; all structural members (rails, legs, posts, purlins, tilt frames and bracing) shall be hot-dip galvanised steel to EN ISO 1461. Stainless-steel or aluminium components in contact with galvanised steel shall be isolated to prevent galvanic corrosion. The structure shall be designed and certified by the contractor to resist the site wind loading to EN 1991-1-4 without exceeding the roof's permissible loading. Every roof penetration shall be sealed and re-waterproofed. All materials and works shall comply with IEC 62548, EN 1991-1-4 (wind) and EN ISO 1461 (latest editions). Measured per PV module supported. | Supply & Install | No. |
| 3.4 | SOL-3.04 | PV mounting structure — ground mounted on concrete bases or curbstone (per module) — 2.7 mm min. member thickness | IEC 62548 / EN 1991-1-4 / EN ISO 1461 | Supply and install a hot-dip galvanised steel ground-mounting structure, with all structural members (posts, purlins, rails and bracing) of not less than 2.7 mm material thickness, and all fixings to support one photovoltaic module on concrete bases, curbstone or screw piles, including posts, purlins, rails, mid and end clamps, cross bracing, adjustable tilt set to the design tilt and azimuth, anchor bolts or cast-in fixings, stainless-steel fasteners, a minimum clearance of 500 mm between the lowest module edge and finished ground level, and the earthing and bonding of the structure to the array earthing conductor. Module mid and end clamps may be of anodised aluminium; all structural members (rails, legs, posts, purlins, tilt frames and bracing) shall be hot-dip galvanised steel to EN ISO 1461. Stainless-steel or aluminium components in contact with galvanised steel shall be isolated to prevent galvanic corrosion. The structure shall be designed and certified by the contractor for the site wind loading to EN 1991-1-4. Concrete bases are measured separately under SOL-2.01. All materials and works shall comply with IEC 62548, EN 1991-1-4 and EN ISO 1461 (latest editions). Measured per PV module supported. | Supply & Install | No. |
| 3.5 | SOL-3.05 | Elevated PV support structure (raised canopy / carport type) over usable ground — 2.7 mm min. steel section thickness | IEC 62548 / EN 1991-1-4 / EN 1993-1-1 | Supply, fabricate, deliver, erect, test and hand over an elevated photovoltaic support structure raising the array clear of the ground so that the area beneath remains usable, with a clear height beneath the lowest structural member of not less than 2.5 metres. The works include a hot-dip galvanised structural steel frame of columns, beams, purlins and bracing with a steel section thickness of not less than 2.7 mm, designed and certified by the contractor's structural engineer to carry the array together with the site wind and, where applicable, snow loading to EN 1991-1-4 and EN 1993-1-1; base plates, holding-down bolts, grouting and connection to the reinforced concrete foundations and excavation measured separately; the module mounting rails, clamps and fixings; cable containment integrated within the structure so that no cable is exposed or unsupported; the earthing and bonding of the complete structure; rainwater run-off control at the array edge; and all shop drawings, structural calculations, welding, surface preparation and galvanising certificates. All materials and works shall comply with IEC 62548, EN 1991-1-4 and EN 1993-1-1. Measured per PV module supported. | Supply & Install | No. |
| 3.6 | SOL-3.06 | Elevated PV support structure (raised canopy / carport type) over usable ground — 5 mm min. steel section thickness | IEC 62548 / EN 1991-1-4 / EN 1993-1-1 | Supply, fabricate, deliver, erect, test and hand over an elevated photovoltaic support structure raising the array clear of the ground so that the area beneath remains usable, with a clear height beneath the lowest structural member of not less than 2.5 metres. The works include a hot-dip galvanised structural steel frame of columns, beams, purlins and bracing with a steel section thickness of not less than 5 mm, designed and certified by the contractor's structural engineer to carry the array together with the site wind and, where applicable, snow loading to EN 1991-1-4 and EN 1993-1-1; base plates, holding-down bolts, grouting and connection to the reinforced concrete foundations and excavation measured separately; the module mounting rails, clamps and fixings; cable containment integrated within the structure so that no cable is exposed or unsupported; the earthing and bonding of the complete structure; rainwater run-off control at the array edge; and all shop drawings, structural calculations, welding, surface preparation and galvanising certificates. All materials and works shall comply with IEC 62548, EN 1991-1-4 and EN 1993-1-1 (latest editions). Measured per PV module supported. | Supply & Install | No. |
| 3.7 | SOL-3.07 | Sandwich panel 5 cm with supporting steel structure — roof / wall to equipment enclosure | EN 14509 | Supply and install an insulated sandwich panel of 50 mm core thickness, with factory-coated steel facings to EN 14509, together with its supporting hot-dip galvanised steel structure of purlins, rails and bracing, to form the roof or wall of an equipment enclosure, shelter or canopy. The works include the design and certification of the supporting structure for the site wind loading, all self-drilling stainless or coated fasteners with sealing washers, ridge, eaves, corner, verge and flashing trims, sealing tapes and mastics at all joints and penetrations, cut-outs formed for cable and pipe entries with sealed collars, and the earthing and bonding of the metal facings and structure. All materials and works shall comply with EN 14509 (latest editions). Measured per square metre of panel on face. | Supply & Install | m² |
| 3.8 | SOL-3.08 | Sandwich panel 10 cm with supporting steel structure — roof / wall to equipment enclosure | EN 14509 | Supply and install an insulated sandwich panel of 100 mm core thickness, with factory-coated steel facings to EN 14509, together with its supporting hot-dip galvanised steel structure, to form the roof or wall of an equipment enclosure where a higher thermal performance is required to keep battery and inverter temperatures within the manufacturer's operating range. The works include the design and certification of the supporting structure for the site wind loading, all fasteners with sealing washers, all trims and flashings, sealing at every joint and penetration, sealed cut-outs for cable and pipe entries, and the earthing and bonding of the metal facings and structure. All materials and works shall comply with EN 14509 (latest editions). Measured per square metre of panel on face. | Supply & Install | m² |
| 3.9 | SOL-3.09 | External steel door (approx. 0.90 × 2.10 m) to inverter / battery / pump room | EN 1627 (security) / EN 14351-1 | Supply and install an external steel door of approximately 0.90 × 2.10 m to an inverter room, battery room, pump house or prefabricated technical housing unit. The works include a galvanised steel frame built in or fixed to the opening, a rigid insulated steel leaf of not less than 1.5 mm sheet with internal stiffeners, three heavy-duty adjustable hinges, a mortise security lock with a cylinder and three keys plus a padlock hasp, a lever handle set, a door closer, a weather bar, threshold and perimeter seals, a louvred or grilled ventilation panel where required for battery-room ventilation, warning and identification signage, the bonding of the door and frame to the earthing system, and priming and two finishing coats of exterior-grade paint in the approved colour. All materials and works shall comply with EN 1627 (security) and EN 14351-1 (latest editions). Measured per door complete. | Supply & Install | No. |
| 3.10 | SOL-3.10 | Steel pole 4 m — for solar luminaire, PV panel or overhead cable support | EN 40 / EN ISO 1461 | Supply and erect a hot-dip galvanised steel pole of 4 m nominal height to carry a solar luminaire, a PV panel, a camera, a cable bracket or an overhead cable span, complete with a concrete foundation, anchor bolts and grouting, a lockable access door with an internal terminal block and cut-out where electrically live, an internal earthing terminal bonded to the earthing system, cable entry, plumbing and alignment, pole-top cap and bracket, and the touching-up of damaged galvanising. All materials and works shall comply with EN 40 and EN ISO 1461 (latest editions). Measured per pole erected. | Supply & Install | No. |
| 3.11 | SOL-3.11 | Steel pole 6 m — for solar luminaire, PV panel or overhead cable support | EN 40 / EN ISO 1461 | Supply and erect a hot-dip galvanised steel pole of 6 m nominal height to carry a solar luminaire, a PV panel, a camera, a cable bracket or an overhead cable span, complete with a concrete foundation designed for the pole height and site wind loading, anchor bolts and grouting, a lockable access door with an internal terminal block and cut-out where electrically live, an internal earthing terminal bonded to the earthing system, cable entry, plumbing and alignment, pole-top cap and bracket, and the touching-up of damaged galvanising. All materials and works shall comply with EN 40 and EN ISO 1461 (latest editions). Measured per pole erected. | Supply & Install | No. |
| 3.12 | SOL-3.12 | Solar LED street lamp 30 W (split type, separate PV panel) | EN 12464-2 / EN 60598 / IP67 | Supply, install, test and hand over a waterproof split-type solar-powered LED street lamp of 30 W rated power for external lighting, with a separate (independent) PV panel, mounted at a height of up to 6 m on a pole measured separately under SOL-3.10 to SOL-3.11. The lamp shall have: an LED luminous flux of not less than 4,200 lm; a lithium iron phosphate (LiFePO₄) battery of not less than 400 Wh at 12.8 V nominal, rated for not less than 2,000 cycles; a monocrystalline PV panel of not less than 80 W; an MPPT charge controller; a microwave motion sensor; an IP67 ingress-protection rating; a charging time of not more than 6 hours in full sun; a discharge time of not less than 20 hours and an autonomy of not less than 2 consecutive nights without charging; an operating temperature range of −15 °C to +70 °C; and a lighting programme of 6 hours at 100% output followed by 6 hours dimmed, with the motion sensor restoring full brightness whenever movement is detected. The works include all brackets, arms, bolts, nuts, screws and accessories needed for installation; orientation of the PV panel towards the sun, clear of shading and obstructions; cable connections; testing and commissioning; and a manufacturer's warranty of not less than 3 years on the luminaire, battery and controller. All materials and works shall comply with EN 60598 and EN 12464-2 (latest editions). Measured per lamp complete. | Supply & Install | No. |
| 3.13 | SOL-3.13 | Solar LED street lamp 50 W (split type, separate PV panel) | EN 12464-2 / EN 60598 / IP67 | Supply, install, test and hand over a waterproof split-type solar-powered LED street lamp of 50 W rated power for external lighting, with a separate (independent) PV panel, mounted at a height of up to 6 m on a pole measured separately under SOL-3.10 to SOL-3.11. The lamp shall have: an LED luminous flux of not less than 7,200 lm; a lithium iron phosphate (LiFePO₄) battery of not less than 600 Wh at 12.8 V nominal, rated for not less than 2,000 cycles; a monocrystalline PV panel of not less than 120 W; an MPPT charge controller; a microwave motion sensor; an IP67 ingress-protection rating; a charging time of not more than 6 hours in full sun; a discharge time of not less than 20 hours and an autonomy of not less than 2 consecutive nights without charging; an operating temperature range of −15 °C to +70 °C; and a lighting programme of 6 hours at 100% output followed by 6 hours dimmed, with the motion sensor restoring full brightness whenever movement is detected. The works include all brackets, arms, bolts, nuts, screws and accessories needed for installation; orientation of the PV panel towards the sun, clear of shading and obstructions; cable connections; testing and commissioning; and a manufacturer's warranty of not less than 3 years on the luminaire, battery and controller. All materials and works shall comply with EN 60598 and EN 12464-2 (latest editions). Measured per lamp complete. | Supply & Install | No. |
|  | SOL-4 INVERTERS, ENERGY STORAGE & REMOVAL OF REDUNDANT EQUIPMENT |  |  |  |  |  |
| 4.1 | SOL-4.01 | Hybrid inverter 3 kW — single-phase (incl. AC/DC protection panel & accessories, and removal of existing inverter where present) | IEC 62109 / IEC 62116 / IEC 61683 | Supply, install, configure, test and commission a 3 kW single-phase hybrid solar inverter of IP65 outdoor rating, pure sine-wave output, dual independent MPPT trackers, battery-ready with a configurable charge profile, and approved for connection alongside the EDL supply. The works include the supply and installation of the AC power cables between the inverter and the distribution board, change-over switch or AC supply point, for a total cable route length of up to 50 m per inverter, in low-voltage copper cable with XLPE or PVC insulation (armoured where buried or exposed), sized to the inverter rating, the permissible voltage drop and the installation method, complete with containment, glands, crimped lugs and terminations (any length beyond 50 m is measured separately under SOL-6.44), a complete AC/DC protection panel dedicated to the inverter (IP54/IP65 enclosure), fully wired and populated with DC isolators and DC circuit breakers, DC string and battery fuses with fuse holders, AC circuit breakers (MCB/MCCB) with residual-current protection, contactors where required for change-over or load control, AC and DC surge protective devices, and all busbars, DIN rails, terminal blocks, earth and neutral bars, cable glands, ferrules, lugs, labels and other accessories needed for a complete and safe installation, the wall or frame mounting bracket with the manufacturer's stated clearances for cooling, DC and AC isolation, string fuses, blocking diodes where required, DC and AC surge protective devices, all power, battery, communication and earthing cabling with glands and ferruled terminations, the configuration of the grid, battery, generator and load-priority parameters to LRC's written operating strategy, firmware updating to the current release, the connection of the monitoring interface, labelling of all circuits, functional and load testing, and the handover of the commissioning report. WHERE AN EXISTING INVERTER IS PRESENT, the works also include its safe isolation, lock-out, disconnection, dismantling, removal and delivery to the LRC store, together with the making good of the wall or frame and the reuse or replacement of the existing cabling as directed by the Engineer. All materials and works shall comply with IEC 62109, IEC 62116 and IEC 61683 (latest editions). Measured per unit, complete and serviceable. | Component | No. |
| 4.2 | SOL-4.02 | Hybrid inverter 5 kW — single-phase (incl. AC/DC protection panel & accessories, and removal of existing inverter where present) | IEC 62109 / IEC 62116 / IEC 61683 | Supply, install, configure, test and commission a 5 kW single-phase hybrid solar inverter of IP65 outdoor rating, pure sine-wave output, dual independent MPPT trackers, battery-ready with a configurable charge profile, and approved for connection alongside the EDL supply. The works include the supply and installation of the AC power cables between the inverter and the distribution board, change-over switch or AC supply point, for a total cable route length of up to 50 m per inverter, in low-voltage copper cable with XLPE or PVC insulation (armoured where buried or exposed), sized to the inverter rating, the permissible voltage drop and the installation method, complete with containment, glands, crimped lugs and terminations (any length beyond 50 m is measured separately under SOL-6.44), a complete AC/DC protection panel dedicated to the inverter (IP54/IP65 enclosure), fully wired and populated with DC isolators and DC circuit breakers, DC string and battery fuses with fuse holders, AC circuit breakers (MCB/MCCB) with residual-current protection, contactors where required for change-over or load control, AC and DC surge protective devices, and all busbars, DIN rails, terminal blocks, earth and neutral bars, cable glands, ferrules, lugs, labels and other accessories needed for a complete and safe installation, the wall or frame mounting bracket with the manufacturer's stated clearances for cooling, DC and AC isolation, string fuses, blocking diodes where required, DC and AC surge protective devices, all power, battery, communication and earthing cabling with glands and ferruled terminations, the configuration of the grid, battery, generator and load-priority parameters to LRC's written operating strategy, firmware updating to the current release, the connection of the monitoring interface, labelling of all circuits, functional and load testing, and the handover of the commissioning report. WHERE AN EXISTING INVERTER IS PRESENT, the works also include its safe isolation, lock-out, disconnection, dismantling, removal and delivery to the LRC store, together with the making good of the wall or frame and the reuse or replacement of the existing cabling as directed by the Engineer. All materials and works shall comply with IEC 62109, IEC 62116 and IEC 61683 (latest editions). Measured per unit, complete and serviceable. | Component | No. |
| 4.3 | SOL-4.03 | Hybrid inverter 8 kW — single-phase (incl. AC/DC protection panel & accessories, and removal of existing inverter where present) | IEC 62109 / IEC 62116 / IEC 61683 | Supply, install, configure, test and commission a 8 kW single-phase hybrid solar inverter of IP65 outdoor rating, pure sine-wave output, dual independent MPPT trackers, battery-ready with a configurable charge profile, and approved for connection alongside the EDL supply. The works include the supply and installation of the AC power cables between the inverter and the distribution board, change-over switch or AC supply point, for a total cable route length of up to 50 m per inverter, in low-voltage copper cable with XLPE or PVC insulation (armoured where buried or exposed), sized to the inverter rating, the permissible voltage drop and the installation method, complete with containment, glands, crimped lugs and terminations (any length beyond 50 m is measured separately under SOL-6.44), a complete AC/DC protection panel dedicated to the inverter (IP54/IP65 enclosure), fully wired and populated with DC isolators and DC circuit breakers, DC string and battery fuses with fuse holders, AC circuit breakers (MCB/MCCB) with residual-current protection, contactors where required for change-over or load control, AC and DC surge protective devices, and all busbars, DIN rails, terminal blocks, earth and neutral bars, cable glands, ferrules, lugs, labels and other accessories needed for a complete and safe installation, the wall or frame mounting bracket with the manufacturer's stated clearances for cooling, DC and AC isolation, string fuses, blocking diodes where required, DC and AC surge protective devices, all power, battery, communication and earthing cabling with glands and ferruled terminations, the configuration of the grid, battery, generator and load-priority parameters to LRC's written operating strategy, firmware updating to the current release, the connection of the monitoring interface, labelling of all circuits, functional and load testing, and the handover of the commissioning report. WHERE AN EXISTING INVERTER IS PRESENT, the works also include its safe isolation, lock-out, disconnection, dismantling, removal and delivery to the LRC store, together with the making good of the wall or frame and the reuse or replacement of the existing cabling as directed by the Engineer. All materials and works shall comply with IEC 62109, IEC 62116 and IEC 61683 (latest editions). Measured per unit, complete and serviceable. | Component | No. |
| 4.4 | SOL-4.04 | Hybrid inverter 10 kW — single-phase (incl. AC/DC protection panel & accessories, and removal of existing inverter where present) | IEC 62109 / IEC 62116 / IEC 61683 | Supply, install, configure, test and commission a 10 kW single-phase hybrid solar inverter of IP65 outdoor rating, pure sine-wave output, dual independent MPPT trackers, battery-ready with a configurable charge profile, and approved for connection alongside the EDL supply. The works include the supply and installation of the AC power cables between the inverter and the distribution board, change-over switch or AC supply point, for a total cable route length of up to 50 m per inverter, in low-voltage copper cable with XLPE or PVC insulation (armoured where buried or exposed), sized to the inverter rating, the permissible voltage drop and the installation method, complete with containment, glands, crimped lugs and terminations (any length beyond 50 m is measured separately under SOL-6.44), a complete AC/DC protection panel dedicated to the inverter (IP54/IP65 enclosure), fully wired and populated with DC isolators and DC circuit breakers, DC string and battery fuses with fuse holders, AC circuit breakers (MCB/MCCB) with residual-current protection, contactors where required for change-over or load control, AC and DC surge protective devices, and all busbars, DIN rails, terminal blocks, earth and neutral bars, cable glands, ferrules, lugs, labels and other accessories needed for a complete and safe installation, the wall or frame mounting bracket with the manufacturer's stated clearances for cooling, DC and AC isolation, string fuses, blocking diodes where required, DC and AC surge protective devices, all power, battery, communication and earthing cabling with glands and ferruled terminations, the configuration of the grid, battery, generator and load-priority parameters to LRC's written operating strategy, firmware updating to the current release, the connection of the monitoring interface, labelling of all circuits, functional and load testing, and the handover of the commissioning report. WHERE AN EXISTING INVERTER IS PRESENT, the works also include its safe isolation, lock-out, disconnection, dismantling, removal and delivery to the LRC store, together with the making good of the wall or frame and the reuse or replacement of the existing cabling as directed by the Engineer. All materials and works shall comply with IEC 62109, IEC 62116 and IEC 61683 (latest editions). Measured per unit, complete and serviceable. | Component | No. |
| 4.5 | SOL-4.05 | Hybrid inverter 12 kW — single-phase (incl. AC/DC protection panel & accessories, and removal of existing inverter where present) | IEC 62109 / IEC 62116 / IEC 61683 | Supply, install, configure, test and commission a 12 kW single-phase hybrid solar inverter of IP65 outdoor rating, pure sine-wave output, dual independent MPPT trackers, battery-ready with a configurable charge profile, and approved for connection alongside the EDL supply. The works include the supply and installation of the AC power cables between the inverter and the distribution board, change-over switch or AC supply point, for a total cable route length of up to 50 m per inverter, in low-voltage copper cable with XLPE or PVC insulation (armoured where buried or exposed), sized to the inverter rating, the permissible voltage drop and the installation method, complete with containment, glands, crimped lugs and terminations (any length beyond 50 m is measured separately under SOL-6.44), a complete AC/DC protection panel dedicated to the inverter (IP54/IP65 enclosure), fully wired and populated with DC isolators and DC circuit breakers, DC string and battery fuses with fuse holders, AC circuit breakers (MCB/MCCB) with residual-current protection, contactors where required for change-over or load control, AC and DC surge protective devices, and all busbars, DIN rails, terminal blocks, earth and neutral bars, cable glands, ferrules, lugs, labels and other accessories needed for a complete and safe installation, the wall or frame mounting bracket with the manufacturer's stated clearances for cooling, DC and AC isolation, string fuses, blocking diodes where required, DC and AC surge protective devices, all power, battery, communication and earthing cabling with glands and ferruled terminations, the configuration of the grid, battery, generator and load-priority parameters to LRC's written operating strategy, firmware updating to the current release, the connection of the monitoring interface, labelling of all circuits, functional and load testing, and the handover of the commissioning report. WHERE AN EXISTING INVERTER IS PRESENT, the works also include its safe isolation, lock-out, disconnection, dismantling, removal and delivery to the LRC store, together with the making good of the wall or frame and the reuse or replacement of the existing cabling as directed by the Engineer. All materials and works shall comply with IEC 62109, IEC 62116 and IEC 61683 (latest editions). Measured per unit, complete and serviceable. | Component | No. |
| 4.6 | SOL-4.06 | Hybrid inverter 16 kW — single-phase (incl. AC/DC protection panel & accessories, and removal of existing inverter where present) | IEC 62109 / IEC 62116 / IEC 61683 | Supply, install, configure, test and commission a 16 kW single-phase hybrid solar inverter of IP65 outdoor rating, pure sine-wave output, dual independent MPPT trackers, battery-ready with a configurable charge profile, and approved for connection alongside the EDL supply. The works include the supply and installation of the AC power cables between the inverter and the distribution board, change-over switch or AC supply point, for a total cable route length of up to 50 m per inverter, in low-voltage copper cable with XLPE or PVC insulation (armoured where buried or exposed), sized to the inverter rating, the permissible voltage drop and the installation method, complete with containment, glands, crimped lugs and terminations (any length beyond 50 m is measured separately under SOL-6.44), a complete AC/DC protection panel dedicated to the inverter (IP54/IP65 enclosure), fully wired and populated with DC isolators and DC circuit breakers, DC string and battery fuses with fuse holders, AC circuit breakers (MCB/MCCB) with residual-current protection, contactors where required for change-over or load control, AC and DC surge protective devices, and all busbars, DIN rails, terminal blocks, earth and neutral bars, cable glands, ferrules, lugs, labels and other accessories needed for a complete and safe installation, the wall or frame mounting bracket with the manufacturer's stated clearances for cooling, DC and AC isolation, string fuses, blocking diodes where required, DC and AC surge protective devices, all power, battery, communication and earthing cabling with glands and ferruled terminations, the configuration of the grid, battery, generator and load-priority parameters to LRC's written operating strategy, firmware updating to the current release, the connection of the monitoring interface, labelling of all circuits, functional and load testing, and the handover of the commissioning report. WHERE AN EXISTING INVERTER IS PRESENT, the works also include its safe isolation, lock-out, disconnection, dismantling, removal and delivery to the LRC store, together with the making good of the wall or frame and the reuse or replacement of the existing cabling as directed by the Engineer. All materials and works shall comply with IEC 62109, IEC 62116 and IEC 61683 (latest editions). Measured per unit, complete and serviceable. | Component | No. |
| 4.7 | SOL-4.07 | Hybrid inverter 5 kW — THREE-PHASE (incl. AC/DC protection panel & accessories, and removal of existing inverter where present) | IEC 62109 / IEC 62116 / IEC 61683 | Supply, install, configure, test and commission a 5 kW three-phase hybrid solar inverter of IP65 outdoor rating, pure sine-wave output, multiple independent MPPT trackers, battery-ready with a configurable charge profile, unbalanced-load capability across the three phases, and approved for connection alongside the EDL supply. The works include the supply and installation of the AC power cables between the inverter and the distribution board, change-over switch or AC supply point, for a total cable route length of up to 50 m per inverter, in low-voltage copper cable with XLPE or PVC insulation (armoured where buried or exposed), sized to the inverter rating, the permissible voltage drop and the installation method, complete with containment, glands, crimped lugs and terminations (any length beyond 50 m is measured separately under SOL-6.44), a complete AC/DC protection panel dedicated to the inverter (IP54/IP65 enclosure), fully wired and populated with DC isolators and DC circuit breakers, DC string and battery fuses with fuse holders, AC circuit breakers (MCB/MCCB) with residual-current protection, contactors where required for change-over or load control, AC and DC surge protective devices, and all busbars, DIN rails, terminal blocks, earth and neutral bars, cable glands, ferrules, lugs, labels and other accessories needed for a complete and safe installation, the mounting bracket with the manufacturer's cooling clearances, three-phase AC isolation and protection, DC isolation, string fuses, DC and AC surge protective devices, phase-sequence and phase-loss protection, all power, battery, communication and earthing cabling with glands and ferruled terminations, parallel or master-slave configuration where more than one unit is installed, the configuration of the grid, battery, generator and load-priority parameters to LRC's written operating strategy, firmware updating, the connection of the monitoring interface, labelling, functional and load testing on all three phases, and the handover of the commissioning report. WHERE AN EXISTING INVERTER IS PRESENT, the works also include its safe isolation, lock-out, disconnection, dismantling, removal and delivery to the LRC store, and the making good of the wall or frame. All materials and works shall comply with IEC 62109, IEC 62116 and IEC 61683 (latest editions). Measured per unit, complete and serviceable. | Component | No. |
| 4.8 | SOL-4.08 | Hybrid inverter 8 kW — THREE-PHASE (incl. AC/DC protection panel & accessories, and removal of existing inverter where present) | IEC 62109 / IEC 62116 / IEC 61683 | Supply, install, configure, test and commission a 8 kW three-phase hybrid solar inverter of IP65 outdoor rating, pure sine-wave output, multiple independent MPPT trackers, battery-ready with a configurable charge profile, unbalanced-load capability across the three phases, and approved for connection alongside the EDL supply. The works include the supply and installation of the AC power cables between the inverter and the distribution board, change-over switch or AC supply point, for a total cable route length of up to 50 m per inverter, in low-voltage copper cable with XLPE or PVC insulation (armoured where buried or exposed), sized to the inverter rating, the permissible voltage drop and the installation method, complete with containment, glands, crimped lugs and terminations (any length beyond 50 m is measured separately under SOL-6.44), a complete AC/DC protection panel dedicated to the inverter (IP54/IP65 enclosure), fully wired and populated with DC isolators and DC circuit breakers, DC string and battery fuses with fuse holders, AC circuit breakers (MCB/MCCB) with residual-current protection, contactors where required for change-over or load control, AC and DC surge protective devices, and all busbars, DIN rails, terminal blocks, earth and neutral bars, cable glands, ferrules, lugs, labels and other accessories needed for a complete and safe installation, the mounting bracket with the manufacturer's cooling clearances, three-phase AC isolation and protection, DC isolation, string fuses, DC and AC surge protective devices, phase-sequence and phase-loss protection, all power, battery, communication and earthing cabling with glands and ferruled terminations, parallel or master-slave configuration where more than one unit is installed, the configuration of the grid, battery, generator and load-priority parameters to LRC's written operating strategy, firmware updating, the connection of the monitoring interface, labelling, functional and load testing on all three phases, and the handover of the commissioning report. WHERE AN EXISTING INVERTER IS PRESENT, the works also include its safe isolation, lock-out, disconnection, dismantling, removal and delivery to the LRC store, and the making good of the wall or frame. All materials and works shall comply with IEC 62109, IEC 62116 and IEC 61683 (latest editions). Measured per unit, complete and serviceable. | Component | No. |
| 4.9 | SOL-4.09 | Hybrid inverter 10 kW — THREE-PHASE (incl. AC/DC protection panel & accessories, and removal of existing inverter where present) | IEC 62109 / IEC 62116 / IEC 61683 | Supply, install, configure, test and commission a 10 kW three-phase hybrid solar inverter of IP65 outdoor rating, pure sine-wave output, multiple independent MPPT trackers, battery-ready with a configurable charge profile, unbalanced-load capability across the three phases, and approved for connection alongside the EDL supply. The works include the supply and installation of the AC power cables between the inverter and the distribution board, change-over switch or AC supply point, for a total cable route length of up to 50 m per inverter, in low-voltage copper cable with XLPE or PVC insulation (armoured where buried or exposed), sized to the inverter rating, the permissible voltage drop and the installation method, complete with containment, glands, crimped lugs and terminations (any length beyond 50 m is measured separately under SOL-6.44), a complete AC/DC protection panel dedicated to the inverter (IP54/IP65 enclosure), fully wired and populated with DC isolators and DC circuit breakers, DC string and battery fuses with fuse holders, AC circuit breakers (MCB/MCCB) with residual-current protection, contactors where required for change-over or load control, AC and DC surge protective devices, and all busbars, DIN rails, terminal blocks, earth and neutral bars, cable glands, ferrules, lugs, labels and other accessories needed for a complete and safe installation, the mounting bracket with the manufacturer's cooling clearances, three-phase AC isolation and protection, DC isolation, string fuses, DC and AC surge protective devices, phase-sequence and phase-loss protection, all power, battery, communication and earthing cabling with glands and ferruled terminations, parallel or master-slave configuration where more than one unit is installed, the configuration of the grid, battery, generator and load-priority parameters to LRC's written operating strategy, firmware updating, the connection of the monitoring interface, labelling, functional and load testing on all three phases, and the handover of the commissioning report. WHERE AN EXISTING INVERTER IS PRESENT, the works also include its safe isolation, lock-out, disconnection, dismantling, removal and delivery to the LRC store, and the making good of the wall or frame. All materials and works shall comply with IEC 62109, IEC 62116 and IEC 61683 (latest editions). Measured per unit, complete and serviceable. | Component | No. |
| 4.10 | SOL-4.10 | Hybrid inverter 12 kW — THREE-PHASE (incl. AC/DC protection panel & accessories, and removal of existing inverter where present) | IEC 62109 / IEC 62116 / IEC 61683 | Supply, install, configure, test and commission a 12 kW three-phase hybrid solar inverter of IP65 outdoor rating, pure sine-wave output, multiple independent MPPT trackers, battery-ready with a configurable charge profile, unbalanced-load capability across the three phases, and approved for connection alongside the EDL supply. The works include the supply and installation of the AC power cables between the inverter and the distribution board, change-over switch or AC supply point, for a total cable route length of up to 50 m per inverter, in low-voltage copper cable with XLPE or PVC insulation (armoured where buried or exposed), sized to the inverter rating, the permissible voltage drop and the installation method, complete with containment, glands, crimped lugs and terminations (any length beyond 50 m is measured separately under SOL-6.44), a complete AC/DC protection panel dedicated to the inverter (IP54/IP65 enclosure), fully wired and populated with DC isolators and DC circuit breakers, DC string and battery fuses with fuse holders, AC circuit breakers (MCB/MCCB) with residual-current protection, contactors where required for change-over or load control, AC and DC surge protective devices, and all busbars, DIN rails, terminal blocks, earth and neutral bars, cable glands, ferrules, lugs, labels and other accessories needed for a complete and safe installation, the mounting bracket with the manufacturer's cooling clearances, three-phase AC isolation and protection, DC isolation, string fuses, DC and AC surge protective devices, phase-sequence and phase-loss protection, all power, battery, communication and earthing cabling with glands and ferruled terminations, parallel or master-slave configuration where more than one unit is installed, the configuration of the grid, battery, generator and load-priority parameters to LRC's written operating strategy, firmware updating, the connection of the monitoring interface, labelling, functional and load testing on all three phases, and the handover of the commissioning report. WHERE AN EXISTING INVERTER IS PRESENT, the works also include its safe isolation, lock-out, disconnection, dismantling, removal and delivery to the LRC store, and the making good of the wall or frame. All materials and works shall comply with IEC 62109, IEC 62116 and IEC 61683 (latest editions). Measured per unit, complete and serviceable. | Component | No. |
| 4.11 | SOL-4.11 | Hybrid inverter 16 kW — THREE-PHASE (incl. AC/DC protection panel & accessories, and removal of existing inverter where present) | IEC 62109 / IEC 62116 / IEC 61683 | Supply, install, configure, test and commission a 16 kW three-phase hybrid solar inverter of IP65 outdoor rating, pure sine-wave output, multiple independent MPPT trackers, battery-ready with a configurable charge profile, unbalanced-load capability across the three phases, and approved for connection alongside the EDL supply. The works include the supply and installation of the AC power cables between the inverter and the distribution board, change-over switch or AC supply point, for a total cable route length of up to 50 m per inverter, in low-voltage copper cable with XLPE or PVC insulation (armoured where buried or exposed), sized to the inverter rating, the permissible voltage drop and the installation method, complete with containment, glands, crimped lugs and terminations (any length beyond 50 m is measured separately under SOL-6.44), a complete AC/DC protection panel dedicated to the inverter (IP54/IP65 enclosure), fully wired and populated with DC isolators and DC circuit breakers, DC string and battery fuses with fuse holders, AC circuit breakers (MCB/MCCB) with residual-current protection, contactors where required for change-over or load control, AC and DC surge protective devices, and all busbars, DIN rails, terminal blocks, earth and neutral bars, cable glands, ferrules, lugs, labels and other accessories needed for a complete and safe installation, the mounting bracket with the manufacturer's cooling clearances, three-phase AC isolation and protection, DC isolation, string fuses, DC and AC surge protective devices, phase-sequence and phase-loss protection, all power, battery, communication and earthing cabling with glands and ferruled terminations, parallel or master-slave configuration where more than one unit is installed, the configuration of the grid, battery, generator and load-priority parameters to LRC's written operating strategy, firmware updating, the connection of the monitoring interface, labelling, functional and load testing on all three phases, and the handover of the commissioning report. WHERE AN EXISTING INVERTER IS PRESENT, the works also include its safe isolation, lock-out, disconnection, dismantling, removal and delivery to the LRC store, and the making good of the wall or frame. All materials and works shall comply with IEC 62109, IEC 62116 and IEC 61683 (latest editions). Measured per unit, complete and serviceable. | Component | No. |
| 4.12 | SOL-4.12 | Hybrid inverter 20 kW — THREE-PHASE (incl. AC/DC protection panel & accessories, and removal of existing inverter where present) | IEC 62109 / IEC 62116 / IEC 61683 | Supply, install, configure, test and commission a 20 kW three-phase hybrid solar inverter of IP65 outdoor rating, pure sine-wave output, multiple independent MPPT trackers, battery-ready with a configurable charge profile, unbalanced-load capability across the three phases, and approved for connection alongside the EDL supply. The works include the supply and installation of the AC power cables between the inverter and the distribution board, change-over switch or AC supply point, for a total cable route length of up to 50 m per inverter, in low-voltage copper cable with XLPE or PVC insulation (armoured where buried or exposed), sized to the inverter rating, the permissible voltage drop and the installation method, complete with containment, glands, crimped lugs and terminations (any length beyond 50 m is measured separately under SOL-6.44), a complete AC/DC protection panel dedicated to the inverter (IP54/IP65 enclosure), fully wired and populated with DC isolators and DC circuit breakers, DC string and battery fuses with fuse holders, AC circuit breakers (MCB/MCCB) with residual-current protection, contactors where required for change-over or load control, AC and DC surge protective devices, and all busbars, DIN rails, terminal blocks, earth and neutral bars, cable glands, ferrules, lugs, labels and other accessories needed for a complete and safe installation, the mounting bracket with the manufacturer's cooling clearances, three-phase AC isolation and protection, DC isolation, string fuses, DC and AC surge protective devices, phase-sequence and phase-loss protection, all power, battery, communication and earthing cabling with glands and ferruled terminations, parallel or master-slave configuration where more than one unit is installed, the configuration of the grid, battery, generator and load-priority parameters to LRC's written operating strategy, firmware updating, the connection of the monitoring interface, labelling, functional and load testing on all three phases, and the handover of the commissioning report. WHERE AN EXISTING INVERTER IS PRESENT, the works also include its safe isolation, lock-out, disconnection, dismantling, removal and delivery to the LRC store, and the making good of the wall or frame. All materials and works shall comply with IEC 62109, IEC 62116 and IEC 61683 (latest editions). Measured per unit, complete and serviceable. | Component | No. |
| 4.13 | SOL-4.13 | Hybrid inverter 15 kW — HIGH-VOLTAGE battery type (incl. AC/DC protection panel & accessories, and removal of existing inverter where present) | IEC 62109 / IEC 62116 / IEC 62619 | Supply, install, configure, test and commission a 15 kW high-voltage-battery hybrid solar inverter of IP65 outdoor rating, designed to operate with a high-voltage lithium battery stack compatible with the provided HV battery, with pure sine-wave output, multiple independent MPPT trackers and communication with the battery management system over the manufacturer's approved protocol. The works include the supply and installation of the AC power cables between the inverter and the distribution board, change-over switch or AC supply point, for a total cable route length of up to 50 m per inverter, in low-voltage copper cable with XLPE or PVC insulation (armoured where buried or exposed), sized to the inverter rating, the permissible voltage drop and the installation method, complete with containment, glands, crimped lugs and terminations (any length beyond 50 m is measured separately under SOL-6.44), a complete AC/DC protection panel dedicated to the inverter (IP54/IP65 enclosure), fully wired and populated with DC isolators and DC circuit breakers, DC string and battery fuses with fuse holders, AC circuit breakers (MCB/MCCB) with residual-current protection, contactors where required for change-over or load control, AC and DC surge protective devices, and all busbars, DIN rails, terminal blocks, earth and neutral bars, cable glands, ferrules, lugs, labels and other accessories needed for a complete and safe installation, the mounting bracket with the manufacturer's cooling clearances, the high-voltage battery isolator and fuse assembly, DC and AC isolation and surge protection, insulation-monitoring and residual-current detection where required by the manufacturer, all power, battery, communication and earthing cabling rated for the battery voltage with glands and ferruled terminations, the commissioning of the inverter-to-BMS communication link and of the charge, discharge and protection parameters to LRC's written operating strategy, firmware updating, monitoring connection, high-voltage warning labelling, functional and load testing, and the handover of the commissioning report. WHERE AN EXISTING INVERTER IS PRESENT, the works also include its safe isolation, lock-out, disconnection, dismantling, removal and delivery to the LRC store. All materials and works shall comply with IEC 62109, IEC 62116 and IEC 62619 (latest editions). Measured per unit, complete and serviceable. | Component | No. |
| 4.14 | SOL-4.14 | Hybrid inverter 20 kW — HIGH-VOLTAGE battery type (incl. AC/DC protection panel & accessories, and removal of existing inverter where present) | IEC 62109 / IEC 62116 / IEC 62619 | Supply, install, configure, test and commission a 20 kW high-voltage-battery hybrid solar inverter of IP65 outdoor rating, designed to operate with a high-voltage lithium battery stack compatible with the provided HV battery, with pure sine-wave output, multiple independent MPPT trackers and communication with the battery management system over the manufacturer's approved protocol. The works include the supply and installation of the AC power cables between the inverter and the distribution board, change-over switch or AC supply point, for a total cable route length of up to 50 m per inverter, in low-voltage copper cable with XLPE or PVC insulation (armoured where buried or exposed), sized to the inverter rating, the permissible voltage drop and the installation method, complete with containment, glands, crimped lugs and terminations (any length beyond 50 m is measured separately under SOL-6.44), a complete AC/DC protection panel dedicated to the inverter (IP54/IP65 enclosure), fully wired and populated with DC isolators and DC circuit breakers, DC string and battery fuses with fuse holders, AC circuit breakers (MCB/MCCB) with residual-current protection, contactors where required for change-over or load control, AC and DC surge protective devices, and all busbars, DIN rails, terminal blocks, earth and neutral bars, cable glands, ferrules, lugs, labels and other accessories needed for a complete and safe installation, the mounting bracket with the manufacturer's cooling clearances, the high-voltage battery isolator and fuse assembly, DC and AC isolation and surge protection, insulation-monitoring and residual-current detection where required by the manufacturer, all power, battery, communication and earthing cabling rated for the battery voltage with glands and ferruled terminations, the commissioning of the inverter-to-BMS communication link and of the charge, discharge and protection parameters to LRC's written operating strategy, firmware updating, monitoring connection, high-voltage warning labelling, functional and load testing, and the handover of the commissioning report. WHERE AN EXISTING INVERTER IS PRESENT, the works also include its safe isolation, lock-out, disconnection, dismantling, removal and delivery to the LRC store. All materials and works shall comply with IEC 62109, IEC 62116 and IEC 62619 (latest editions). Measured per unit, complete and serviceable. | Component | No. |
| 4.15 | SOL-4.15 | Hybrid inverter 25 kW — HIGH-VOLTAGE battery type (incl. AC/DC protection panel & accessories, and removal of existing inverter where present) | IEC 62109 / IEC 62116 / IEC 62619 | Supply, install, configure, test and commission a 25 kW high-voltage-battery hybrid solar inverter of IP65 outdoor rating, designed to operate with a high-voltage lithium battery stack compatible with the provided HV battery, with pure sine-wave output, multiple independent MPPT trackers and communication with the battery management system over the manufacturer's approved protocol. The works include the supply and installation of the AC power cables between the inverter and the distribution board, change-over switch or AC supply point, for a total cable route length of up to 50 m per inverter, in low-voltage copper cable with XLPE or PVC insulation (armoured where buried or exposed), sized to the inverter rating, the permissible voltage drop and the installation method, complete with containment, glands, crimped lugs and terminations (any length beyond 50 m is measured separately under SOL-6.44), a complete AC/DC protection panel dedicated to the inverter (IP54/IP65 enclosure), fully wired and populated with DC isolators and DC circuit breakers, DC string and battery fuses with fuse holders, AC circuit breakers (MCB/MCCB) with residual-current protection, contactors where required for change-over or load control, AC and DC surge protective devices, and all busbars, DIN rails, terminal blocks, earth and neutral bars, cable glands, ferrules, lugs, labels and other accessories needed for a complete and safe installation, the mounting bracket with the manufacturer's cooling clearances, the high-voltage battery isolator and fuse assembly, DC and AC isolation and surge protection, insulation-monitoring and residual-current detection where required by the manufacturer, all power, battery, communication and earthing cabling rated for the battery voltage with glands and ferruled terminations, the commissioning of the inverter-to-BMS communication link and of the charge, discharge and protection parameters to LRC's written operating strategy, firmware updating, monitoring connection, high-voltage warning labelling, functional and load testing, and the handover of the commissioning report. WHERE AN EXISTING INVERTER IS PRESENT, the works also include its safe isolation, lock-out, disconnection, dismantling, removal and delivery to the LRC store. All materials and works shall comply with IEC 62109, IEC 62116 and IEC 62619 (latest editions). Measured per unit, complete and serviceable. | Component | No. |
| 4.16 | SOL-4.16 | Hybrid inverter 30 kW — HIGH-VOLTAGE battery type (incl. AC/DC protection panel & accessories, and removal of existing inverter where present) | IEC 62109 / IEC 62116 / IEC 62619 | Supply, install, configure, test and commission a 30 kW high-voltage-battery hybrid solar inverter of IP65 outdoor rating, designed to operate with a high-voltage lithium battery stack compatible with the provided HV battery, with pure sine-wave output, multiple independent MPPT trackers and communication with the battery management system over the manufacturer's approved protocol. The works include the supply and installation of the AC power cables between the inverter and the distribution board, change-over switch or AC supply point, for a total cable route length of up to 50 m per inverter, in low-voltage copper cable with XLPE or PVC insulation (armoured where buried or exposed), sized to the inverter rating, the permissible voltage drop and the installation method, complete with containment, glands, crimped lugs and terminations (any length beyond 50 m is measured separately under SOL-6.44), a complete AC/DC protection panel dedicated to the inverter (IP54/IP65 enclosure), fully wired and populated with DC isolators and DC circuit breakers, DC string and battery fuses with fuse holders, AC circuit breakers (MCB/MCCB) with residual-current protection, contactors where required for change-over or load control, AC and DC surge protective devices, and all busbars, DIN rails, terminal blocks, earth and neutral bars, cable glands, ferrules, lugs, labels and other accessories needed for a complete and safe installation, the mounting bracket with the manufacturer's cooling clearances, the high-voltage battery isolator and fuse assembly, DC and AC isolation and surge protection, insulation-monitoring and residual-current detection where required by the manufacturer, all power, battery, communication and earthing cabling rated for the battery voltage with glands and ferruled terminations, the commissioning of the inverter-to-BMS communication link and of the charge, discharge and protection parameters to LRC's written operating strategy, firmware updating, monitoring connection, high-voltage warning labelling, functional and load testing, and the handover of the commissioning report. WHERE AN EXISTING INVERTER IS PRESENT, the works also include its safe isolation, lock-out, disconnection, dismantling, removal and delivery to the LRC store. All materials and works shall comply with IEC 62109, IEC 62116 and IEC 62619 (latest editions). Measured per unit, complete and serviceable. | Component | No. |
| 4.17 | SOL-4.17 | Hybrid inverter 40 kW — HIGH-VOLTAGE battery type (incl. AC/DC protection panel & accessories, and removal of existing inverter where present) | IEC 62109 / IEC 62116 / IEC 62619 | Supply, install, configure, test and commission a 40 kW high-voltage-battery hybrid solar inverter of IP65 outdoor rating, designed to operate with a high-voltage lithium battery stack compatible with the provided HV battery, with pure sine-wave output, multiple independent MPPT trackers and communication with the battery management system over the manufacturer's approved protocol. The works include the supply and installation of the AC power cables between the inverter and the distribution board, change-over switch or AC supply point, for a total cable route length of up to 50 m per inverter, in low-voltage copper cable with XLPE or PVC insulation (armoured where buried or exposed), sized to the inverter rating, the permissible voltage drop and the installation method, complete with containment, glands, crimped lugs and terminations (any length beyond 50 m is measured separately under SOL-6.44), a complete AC/DC protection panel dedicated to the inverter (IP54/IP65 enclosure), fully wired and populated with DC isolators and DC circuit breakers, DC string and battery fuses with fuse holders, AC circuit breakers (MCB/MCCB) with residual-current protection, contactors where required for change-over or load control, AC and DC surge protective devices, and all busbars, DIN rails, terminal blocks, earth and neutral bars, cable glands, ferrules, lugs, labels and other accessories needed for a complete and safe installation, the mounting bracket with the manufacturer's cooling clearances, the high-voltage battery isolator and fuse assembly, DC and AC isolation and surge protection, insulation-monitoring and residual-current detection where required by the manufacturer, all power, battery, communication and earthing cabling rated for the battery voltage with glands and ferruled terminations, the commissioning of the inverter-to-BMS communication link and of the charge, discharge and protection parameters to LRC's written operating strategy, firmware updating, monitoring connection, high-voltage warning labelling, functional and load testing, and the handover of the commissioning report. WHERE AN EXISTING INVERTER IS PRESENT, the works also include its safe isolation, lock-out, disconnection, dismantling, removal and delivery to the LRC store. All materials and works shall comply with IEC 62109, IEC 62116 and IEC 62619 (latest editions). Measured per unit, complete and serviceable. | Component | No. |
| 4.18 | SOL-4.18 | Hybrid inverter 50 kW — HIGH-VOLTAGE battery type (incl. AC/DC protection panel & accessories, and removal of existing inverter where present) | IEC 62109 / IEC 62116 / IEC 62619 | Supply, install, configure, test and commission a 50 kW high-voltage-battery hybrid solar inverter of IP65 outdoor rating, designed to operate with a high-voltage lithium battery stack compatible with the provided HV battery, with pure sine-wave output, multiple independent MPPT trackers and communication with the battery management system over the manufacturer's approved protocol. The works include the supply and installation of the AC power cables between the inverter and the distribution board, change-over switch or AC supply point, for a total cable route length of up to 50 m per inverter, in low-voltage copper cable with XLPE or PVC insulation (armoured where buried or exposed), sized to the inverter rating, the permissible voltage drop and the installation method, complete with containment, glands, crimped lugs and terminations (any length beyond 50 m is measured separately under SOL-6.44), a complete AC/DC protection panel dedicated to the inverter (IP54/IP65 enclosure), fully wired and populated with DC isolators and DC circuit breakers, DC string and battery fuses with fuse holders, AC circuit breakers (MCB/MCCB) with residual-current protection, contactors where required for change-over or load control, AC and DC surge protective devices, and all busbars, DIN rails, terminal blocks, earth and neutral bars, cable glands, ferrules, lugs, labels and other accessories needed for a complete and safe installation, the mounting bracket with the manufacturer's cooling clearances, the high-voltage battery isolator and fuse assembly, DC and AC isolation and surge protection, insulation-monitoring and residual-current detection where required by the manufacturer, all power, battery, communication and earthing cabling rated for the battery voltage with glands and ferruled terminations, the commissioning of the inverter-to-BMS communication link and of the charge, discharge and protection parameters to LRC's written operating strategy, firmware updating, monitoring connection, high-voltage warning labelling, functional and load testing, and the handover of the commissioning report. WHERE AN EXISTING INVERTER IS PRESENT, the works also include its safe isolation, lock-out, disconnection, dismantling, removal and delivery to the LRC store. All materials and works shall comply with IEC 62109, IEC 62116 and IEC 62619 (latest editions). Measured per unit, complete and serviceable. | Component | No. |
| 4.19 | SOL-4.19 | Hybrid inverter 60 kW — HIGH-VOLTAGE battery type (incl. AC/DC protection panel & accessories, and removal of existing inverter where present) | IEC 62109 / IEC 62116 / IEC 62619 | Supply, install, configure, test and commission a 60 kW high-voltage-battery hybrid solar inverter of IP65 outdoor rating, designed to operate with a high-voltage lithium battery stack compatible with the provided HV battery, with pure sine-wave output, multiple independent MPPT trackers and communication with the battery management system over the manufacturer's approved protocol. The works include the supply and installation of the AC power cables between the inverter and the distribution board, change-over switch or AC supply point, for a total cable route length of up to 50 m per inverter, in low-voltage copper cable with XLPE or PVC insulation (armoured where buried or exposed), sized to the inverter rating, the permissible voltage drop and the installation method, complete with containment, glands, crimped lugs and terminations (any length beyond 50 m is measured separately under SOL-6.44), a complete AC/DC protection panel dedicated to the inverter (IP54/IP65 enclosure), fully wired and populated with DC isolators and DC circuit breakers, DC string and battery fuses with fuse holders, AC circuit breakers (MCB/MCCB) with residual-current protection, contactors where required for change-over or load control, AC and DC surge protective devices, and all busbars, DIN rails, terminal blocks, earth and neutral bars, cable glands, ferrules, lugs, labels and other accessories needed for a complete and safe installation, the mounting bracket with the manufacturer's cooling clearances, the high-voltage battery isolator and fuse assembly, DC and AC isolation and surge protection, insulation-monitoring and residual-current detection where required by the manufacturer, all power, battery, communication and earthing cabling rated for the battery voltage with glands and ferruled terminations, the commissioning of the inverter-to-BMS communication link and of the charge, discharge and protection parameters to LRC's written operating strategy, firmware updating, monitoring connection, high-voltage warning labelling, functional and load testing, and the handover of the commissioning report. WHERE AN EXISTING INVERTER IS PRESENT, the works also include its safe isolation, lock-out, disconnection, dismantling, removal and delivery to the LRC store. All materials and works shall comply with IEC 62109, IEC 62116 and IEC 62619 (latest editions). Measured per unit, complete and serviceable. | Component | No. |
| 4.20 | SOL-4.20 | Hybrid inverter 80 kW — HIGH-VOLTAGE battery type (incl. AC/DC protection panel & accessories, and removal of existing inverter where present) | IEC 62109 / IEC 62116 / IEC 62619 | Supply, install, configure, test and commission a 80 kW high-voltage-battery hybrid solar inverter of IP65 outdoor rating, designed to operate with a high-voltage lithium battery stack compatible with the provided HV battery, with pure sine-wave output, multiple independent MPPT trackers and communication with the battery management system over the manufacturer's approved protocol. The works include the supply and installation of the AC power cables between the inverter and the distribution board, change-over switch or AC supply point, for a total cable route length of up to 50 m per inverter, in low-voltage copper cable with XLPE or PVC insulation (armoured where buried or exposed), sized to the inverter rating, the permissible voltage drop and the installation method, complete with containment, glands, crimped lugs and terminations (any length beyond 50 m is measured separately under SOL-6.44), a complete AC/DC protection panel dedicated to the inverter (IP54/IP65 enclosure), fully wired and populated with DC isolators and DC circuit breakers, DC string and battery fuses with fuse holders, AC circuit breakers (MCB/MCCB) with residual-current protection, contactors where required for change-over or load control, AC and DC surge protective devices, and all busbars, DIN rails, terminal blocks, earth and neutral bars, cable glands, ferrules, lugs, labels and other accessories needed for a complete and safe installation, the mounting bracket with the manufacturer's cooling clearances, the high-voltage battery isolator and fuse assembly, DC and AC isolation and surge protection, insulation-monitoring and residual-current detection where required by the manufacturer, all power, battery, communication and earthing cabling rated for the battery voltage with glands and ferruled terminations, the commissioning of the inverter-to-BMS communication link and of the charge, discharge and protection parameters to LRC's written operating strategy, firmware updating, monitoring connection, high-voltage warning labelling, functional and load testing, and the handover of the commissioning report. WHERE AN EXISTING INVERTER IS PRESENT, the works also include its safe isolation, lock-out, disconnection, dismantling, removal and delivery to the LRC store. All materials and works shall comply with IEC 62109, IEC 62116 and IEC 62619 (latest editions). Measured per unit, complete and serviceable. | Component | No. |
| 4.21 | SOL-4.21 | Lithium battery 48–52 V 100 Ah (LFP with integral BMS) | IEC 62619 / IEC 62620 / UN 38.3 | Supply, install, configure, test and commission a 48–52 V nominal 100 Ah lithium iron phosphate (LFP) battery with an integral battery management system providing cell balancing and over-voltage, under-voltage, over-current, short-circuit and over- and under-temperature protection, UN 38.3 transport certified, with a cycle life of not less than 6,000 cycles at 80% depth of discharge. The works include wall, floor or rack mounting with the manufacturer's clearances, the battery isolator and fuse or breaker sized to the manufacturer's requirement, correctly sized and colour-coded interconnection cabling with crimped and insulated lugs and torque-marked terminals, the communication cable and the commissioning of the BMS-to-inverter protocol, polarity and insulation verification, a capacity and charge/discharge test recorded in the commissioning report, polarity and hazard labelling, and the handover of the warranty certificate. All materials and works shall comply with IEC 62619, IEC 62620 and UN 38.3 (latest editions). Measured per unit, complete and serviceable. | Component | No. |
| 4.22 | SOL-4.22 | Lithium battery 48–52 V 200 Ah (LFP with integral BMS) | IEC 62619 / IEC 62620 / UN 38.3 | Supply, install, configure, test and commission a 48–52 V nominal 200 Ah lithium iron phosphate (LFP) battery with an integral battery management system providing cell balancing and over-voltage, under-voltage, over-current, short-circuit and over- and under-temperature protection, UN 38.3 transport certified, with a cycle life of not less than 6,000 cycles at 80% depth of discharge. The works include wall, floor or rack mounting with the manufacturer's clearances, the battery isolator and fuse or breaker sized to the manufacturer's requirement, correctly sized and colour-coded interconnection cabling with crimped and insulated lugs and torque-marked terminals, the communication cable and the commissioning of the BMS-to-inverter protocol, polarity and insulation verification, a capacity and charge/discharge test recorded in the commissioning report, polarity and hazard labelling, and the handover of the warranty certificate. All materials and works shall comply with IEC 62619, IEC 62620 and UN 38.3 (latest editions). Measured per unit, complete and serviceable. | Component | No. |
| 4.23 | SOL-4.23 | Lithium battery 48–52 V 300 Ah (LFP with integral BMS) | IEC 62619 / IEC 62620 / UN 38.3 | Supply, install, configure, test and commission a 48–52 V nominal 300 Ah lithium iron phosphate (LFP) battery with an integral battery management system providing cell balancing and over-voltage, under-voltage, over-current, short-circuit and over- and under-temperature protection, UN 38.3 transport certified, with a cycle life of not less than 6,000 cycles at 80% depth of discharge. The works include wall, floor or rack mounting with the manufacturer's clearances, the battery isolator and fuse or breaker sized to the manufacturer's requirement, correctly sized and colour-coded interconnection cabling with crimped and insulated lugs and torque-marked terminals, the communication cable and the commissioning of the BMS-to-inverter protocol, polarity and insulation verification, a capacity and charge/discharge test recorded in the commissioning report, polarity and hazard labelling, and the handover of the warranty certificate. All materials and works shall comply with IEC 62619, IEC 62620 and UN 38.3 (latest editions). Measured per unit, complete and serviceable. | Component | No. |
| 4.24 | SOL-4.24 | Rack-mounted lithium battery 48–52 V 100 Ah (LFP with integral BMS) | IEC 62619 / UN 38.3 | Supply, install, configure, test and commission a rack-mounted 48–52 V nominal 100 Ah lithium iron phosphate (LFP) battery module with an integral battery management system, sized to a standard 19-inch equipment rack, complete with front-panel status indication and an isolating breaker. The works include the supply and installation of a manufacturer-approved 19-inch battery racking system (powder-coated steel rack or cabinet with adjustable rails, cable management, ventilation clearances, earthing and bonding, and floor or wall anchoring with anti-tip restraint), insertion and securing in the rack, the parallel interconnection busbars or cables with crimped lugs and torque marking, the setting of the module address and the commissioning of the parallel BMS communication chain, the master-module and inverter communication link, polarity and insulation verification, a recorded capacity test, labelling, and the handover of the warranty certificate. All materials and works shall comply with IEC 62619 and UN 38.3 (latest editions). Measured per battery module. | Component | No. |
| 4.25 | SOL-4.25 | HIGH-VOLTAGE lithium battery module (LFP, stackable, >200 V DC nominal) — per kWh | IEC 62619 / IEC 62620 / UN 38.3 | Supply, install, configure, test and commission a high-voltage stackable lithium iron phosphate (LFP) battery module forming part of a high-voltage battery stack of not less than 200 V DC nominal, with an integral module management board, cell balancing and full protection against over-voltage, under-voltage, over-current, short circuit and temperature excursion, UN 38.3 transport certified, with a cycle life of not less than 6,000 cycles at 80% depth of discharge. The works include the supply and installation of a manufacturer-approved battery racking system (stacking frame or rack with base plinth, powder-coated steel, earthing and bonding, cable management, ventilation clearances, and floor or wall anchoring with anti-tip and seismic restraint), stacking and mechanical securing to the manufacturer's base unit with all inter-module power and communication connectors, high-voltage rated interconnection with insulated and shrouded terminations, the commissioning of the stack addressing and of the BMS-to-inverter communication protocol, insulation-resistance and polarity verification at stack voltage, a recorded capacity and charge/discharge test, high-voltage hazard labelling in Arabic and English, and the handover of the warranty certificate. All materials and works shall comply with IEC 62619, IEC 62620 and UN 38.3 (latest editions). Measured per kilowatt-hour of nominal usable capacity installed. compatible with provided HV inverter | Component | kWh |
| 4.26 | SOL-4.26 | HIGH-VOLTAGE battery base / master control unit with high-voltage box | IEC 62619 / IEC 62477-1 | Supply, install, configure, test and commission the base or master control unit of a high-voltage battery stack, incorporating the stack management system, the high-voltage disconnect and pre-charge circuit, the main DC fuse and contactor, insulation monitoring, the inverter communication interface and the stack status indication. The works include the supply and installation of the manufacturer-approved racking system for the complete stack (frame or cabinet with base, powder-coated steel, earthing and bonding, cable management, ventilation clearances and anchoring), the floor-standing or wall base with seismic and anti-tip restraint, the high-voltage DC cabling to the inverter with shrouded and rated connectors, the earthing and bonding of the enclosure, the configuration of the stack parameters and the inverter communication protocol, insulation and functional testing at stack voltage, emergency-shutdown provision, high-voltage hazard labelling, and the handover of the commissioning record. All materials and works shall comply with IEC 62619 and IEC 62477-1 (latest editions). Measured per stack. | Component | No. |
|  | SOL-5 ELECTRICAL WORKS, CONTAINMENT, PROTECTION & DISTRIBUTION |  |  |  |  |  |
| 5.1 | SOL-5.01 | DC combiner box (IP54/IP65, fused, with string monitoring provision) | IEC 61439-2 / IEC 62548 | Supply, install, wire, test and hand over a DC string combiner box in a weatherproof enclosure of not less than IP54 (IP65 where exposed), UV-stabilised and lockable, complete with the number of string ways required by the array. The works include gPV string fuses and holders in both the positive and the negative poles rated to the module reverse-current specification, a load-break DC isolator on the outgoing combined circuit, a Type 2 DC surge protective device with a status indicator referenced to the array earth, busbars and terminals rated to the array short-circuit current, provision for string current monitoring, all cable glands, internal wiring with ferruled terminations, an internal wiring diagram fixed inside the lid, string identification and polarity labels, arc-flash and 'live DC after isolation of AC' warning labelling, the earthing and bonding of the enclosure and gland plate, and polarity, insulation and functional testing. All materials and works shall comply with IEC 61439-2 and IEC 62548 (latest editions). Measured per unit, complete and serviceable. | Component | No. |
| 5.2 | SOL-5.02 | AC/DC protection enclosure with surge protective devices (SPDs) | IEC 61643-11 / IEC 61643-31 / IEC 61439-2 | Supply, install, wire, test and hand over a combined AC/DC protection enclosure of not less than IP54, lockable and UV-stabilised, housing the surge and overcurrent protection for the solar installation. The works include a Type 2 (or Type 1+2 where a lightning protection system is present) AC surge protective device on the incoming and outgoing AC circuits and a Type 2 DC surge protective device on the array circuits, each with a visual status indicator and a backup fuse, AC miniature circuit breakers or moulded-case breakers and DC isolators as required, earth and neutral bars, short and direct earthing conductors to the main earth bar with the connecting leads kept to the minimum practicable length, all glands and internal wiring with ferruled terminations, a wiring diagram fixed inside the lid, circuit labelling and hazard warnings, the earthing and bonding of the enclosure, and functional and insulation testing. All materials and works shall comply with IEC 61643-11, IEC 61643-31 and IEC 61439-2 (latest editions). Measured per unit, complete and serviceable. | Component | No. |
| 5.3 | SOL-5.03 | Inverter protection enclosure (IP54/IP65) — AC and DC isolation local to the inverter | IEC 61439-2 | Supply, install, wire, test and hand over a protection enclosure local to the inverter, of not less than IP54 (IP65 where outdoors), lockable and UV-stabilised, containing the lockable DC isolator and the lockable AC isolator required to make the inverter safe for maintenance, together with the inverter output circuit breaker, blocking diodes and surge protective devices where required, all glands, internal wiring with ferruled terminations, earth bar and bonding, a wiring diagram inside the lid, 'isolate both AC and DC' warning labelling, and functional testing including the proving of isolation. All materials and works shall comply with IEC 61439-2 (latest editions). Measured per unit, complete and serviceable. | Component | No. |
| 5.4 | SOL-5.04 | Monitoring, control & remote data-logging — complete per system | IEC 61724-1 | Supply, install, configure, test and hand over a local monitoring and control panel for a solar installation, comprising the data logger or communication gateway, the irradiance and module and ambient temperature sensors where required, current and voltage transducers or an energy meter on the AC and DC sides, the inverter and battery communication interfaces, a local display of generation, consumption, battery state of charge and alarm status, the configuration of alarm set points and the recording interval, all sensor and communication cabling, glands and enclosure, and the demonstration of the panel to LRC staff. All materials and works shall comply with IEC 61724-1 (latest editions). Measured per panel, complete and serviceable. The item covers the local monitoring panel and its sensors AND the remote platform alarm rules for inverter fault, communication loss, low state of charge and abnormal generation, logging at intervals not exceeding 15 minutes with not less than 12 months of retained history and CSV export, remote access credentials issued to LRC, a written guide for LRC staff, and the first 12 months of platform and data subscription. | Component | No. |
| 5.5 | SOL-5.05 | Earthing system for a solar installation — electrodes, conductors & bonding (≤5 Ω) | IEC 60364-5-54 / IEC 62548 | Supply, install, test and hand over a complete earthing system for a solar installation achieving a measured earth resistance not exceeding 5 ohms. The works include copper-bonded steel earth electrodes driven to the depth required, an inspection pit with a removable cover at each electrode, bare or insulated copper earthing conductors sized to the main supply and to IEC 60364-5-54, exothermic or approved mechanical connections, earth-enhancing compound where the soil resistivity requires it, a main earth bar with disconnecting links, the bonding of every module frame, mounting rail, metal enclosure, cabinet, cable tray, pole, tank and pipe associated with the installation, the equipotential bonding of the equipment room, the measurement of the earth resistance by the fall-of-potential method with a calibrated instrument, and the issue of a signed test record stating the measured value, the instrument and the date. All materials and works shall comply with IEC 60364-5-54 and IEC 62548 (latest editions). Measured per complete system. | Supply & Install | No. |
| 5.6 | SOL-5.06 | Lightning protection system for a solar installation (structures up to 4 floors) | IEC 62305 / IEC 62561 | Supply, install, test and hand over a lightning protection system for a building or structure carrying a solar installation, designed in accordance with IEC 62305 following a documented risk assessment. The works include air terminals positioned so that the PV array falls within the protected volume without casting shade on the modules, down-conductors on the shortest practicable routes with test joints, a ring or rod earth termination network bonded to the main earthing system, the maintenance of the separation distance from the PV array and its cabling or, where this cannot be achieved, the equipotential bonding of the array in accordance with the standard, surge protective devices coordinated with those in the AC and DC enclosures, all fixings, clamps and corrosion-compatible connections, the continuity and earth-resistance testing of the completed installation, and the issue of a signed test record and an as-installed layout drawing. All materials and works shall comply with IEC 62305 and IEC 62561 (latest editions). Measured per complete system. | Supply & Install | No. |
| 5.7 | SOL-5.07 | Change-over / transfer switch — manual (MTS) AND automatic (ATS), single- or three-phase, up to 4 × 400 A, in IP54 panel (EDL / generator / solar) | IEC 60947-6-1 / IEC 60947-3 / IEC 61439-2 | Supply, install, wire, test and commission a change-over (transfer) switch to select safely between the EDL mains, the generator and the solar/inverter supply, rated to the full connected load as stated in the call-off order up to 400 A, double-pole on single-phase or four-pole on three-phase systems, mounted in an IP54 floor-standing or wall-mounted panel. The unit shall provide BOTH manual and automatic operation, that is an automatic transfer switch with adjustable voltage and frequency sensing and adjustable transfer and re-transfer time delays operating on the loss or restoration of the preferred source, together with a manual transfer function (manual override or bypass handle, or a load-break manual transfer switch with a positive-break mechanism) allowing an operator to select any source by hand with the controller de-energised. The works include mechanical and electrical interlocks preventing the paralleling of sources, source-available, position and phase-sequence indication, incoming and outgoing busbars and cable terminals rated to the switch current, cable glands and supports, earth and neutral bars, all power and control cabling and internal wiring with ferruled terminations, the earthing and bonding of the panel, complete labelling of sources and positions, a laminated single-line diagram and operating instruction fixed inside the door, and the functional testing under load and recording of BOTH the automatic and the manual modes on completion. All materials and works shall comply with IEC 60947-6-1, IEC 60947-3 and IEC 61439-2 (latest editions). Measured per unit, complete and serviceable. | Supply & Install | No. |
| 5.8 | SOL-5.08 | Main distribution board (12–24 way, populated, all devices double-pole) | IEC 61439-3 | Supply, install, wire, test and hand over a main distribution board of 12 to 24 ways in an IP-rated enclosure, complete with a main switch or incomer, miniature circuit breakers and RCBOs, busbar, earth and neutral bars, DIN rails, blanking plates and a hinged lockable cover. ALL protective devices on single-phase circuits shall be DOUBLE-POLE, switching both the line and the neutral; single-pole devices are not acceptable. The works include the full wiring of every circuit with ferruled and numbered terminations, complete and durable circuit labelling and a typed schedule fixed inside the cover, the segregation of the solar, generator and mains circuits with clear identification, warning labelling of the dual supply, the earthing and bonding of the board, and inspection and testing to IEC 60364-6 with a certificate. All materials and works shall comply with IEC 61439-3 (latest editions). Measured per board, complete and serviceable. | Supply & Install | No. |
| 5.9 | SOL-5.09 | Circuit breaker box (6-way, double-pole devices) | IEC 61439-3 | Supply, install, wire, test and hand over a 6-way circuit breaker box complete with the enclosure, DIN rail, busbar, earth and neutral bars and appropriately rated breakers. ALL protective devices on single-phase circuits shall be DOUBLE-POLE, switching both line and neutral; single-pole devices are not acceptable. The works include full wiring with ferruled terminations, durable circuit labelling and a schedule inside the cover, earthing and bonding, and testing on completion. All materials and works shall comply with IEC 61439-3 (latest editions). Measured per unit, complete and serviceable. | Supply & Install | No. |
| 5.10 | SOL-5.10 | Contactor — four-pole (3P+N), 40 A (AC-1), 230 V AC coil, with auxiliary contacts | IEC 60947-4-1 | Supply and install a four-pole (3P+N) AC power contactor rated 40 A in utilisation category AC-1 (non-inductive / slightly inductive loads, distribution and change-over duty) at 400 V, switching all three lines and neutral, with a 230 V AC operating coil (or coil voltage to suit the control circuit where instructed), and not less than 1 NO + 1 NC auxiliary contacts, for the switching of generator, change-over, load-shedding or general distribution circuits, mounted on DIN rail or mounting plate within the panel. Where the contactor directly switches a motor (direct-on-line pump or fan), it shall in addition carry an AC-3 rating not less than the motor full-load current, confirmed by the manufacturer's data sheet. The works include power and control wiring with ferruled terminations, integration with the existing control circuit, durable labelling and functional testing. All materials and works shall comply with IEC 60947-4-1 (latest editions). Measured per device. | Supply & Install | No. |
| 5.11 | SOL-5.11 | Copper wiring circuit 1.5 mm² — concealed conduit (final circuits) | IEC 60364 / IEC 60227 | Supply and install a final circuit of copper conductors drawn into heavy-duty PVC conduit of not less than 20 mm concealed in chases or within the building fabric, including the chasing and making good of walls, the conduit, bends, couplers, saddles, junction boxes and back-boxes, draw wires, colour-coded single-core copper line, neutral and protective conductors of 1.5 mm² cross-section, terminations, circuit identification, and continuity, insulation-resistance and polarity testing on completion. All materials and works shall comply with IEC 60364 and IEC 60227 (latest editions). Measured per linear metre of completed 1.5 mm² circuit. | Supply & Install | m |
| 5.12 | SOL-5.12 | Copper wiring circuit 2.5 mm² — concealed conduit (final circuits) | IEC 60364 / IEC 60227 | Supply and install a final circuit of copper conductors drawn into heavy-duty PVC conduit of not less than 20 mm concealed in chases or within the building fabric, including the chasing and making good of walls, the conduit, bends, couplers, saddles, junction boxes and back-boxes, draw wires, colour-coded single-core copper line, neutral and protective conductors of 2.5 mm² cross-section, terminations, circuit identification, and continuity, insulation-resistance and polarity testing on completion. All materials and works shall comply with IEC 60364 and IEC 60227 (latest editions). Measured per linear metre of completed 2.5 mm² circuit. | Supply & Install | m |
| 5.13 | SOL-5.13 | Copper wiring circuit 4 mm² — concealed conduit (final circuits) | IEC 60364 / IEC 60227 | Supply and install a final circuit of copper conductors drawn into heavy-duty PVC conduit of not less than 25 mm concealed in chases or within the building fabric, including the chasing and making good of walls, the conduit, bends, couplers, saddles, junction boxes and back-boxes, draw wires, colour-coded single-core copper line, neutral and protective conductors of 4 mm² cross-section, terminations, circuit identification, and continuity, insulation-resistance and polarity testing on completion. All materials and works shall comply with IEC 60364 and IEC 60227 (latest editions). Measured per linear metre of completed 4 mm² circuit. | Supply & Install | m |
| 5.14 | SOL-5.14 | Copper wiring circuit 6 mm² — concealed conduit (final circuits) | IEC 60364 / IEC 60227 | Supply and install a final circuit of copper conductors drawn into heavy-duty PVC conduit of not less than 25 mm concealed in chases or within the building fabric, including the chasing and making good of walls, the conduit, bends, couplers, saddles, junction boxes and back-boxes, draw wires, colour-coded single-core copper line, neutral and protective conductors of 6 mm² cross-section, terminations, circuit identification, and continuity, insulation-resistance and polarity testing on completion. All materials and works shall comply with IEC 60364 and IEC 60227 (latest editions). Measured per linear metre of completed 6 mm² circuit. | Supply & Install | m |
| 5.15 | SOL-5.15 | Copper wiring circuit 1.5 mm² — surface conduit / trunking (final circuits) | IEC 60364 / IEC 60227 | Supply and install a final circuit of copper conductors in heavy-duty PVC or steel conduit of not less than 20 mm or trunking fixed on the surface, including the conduit or trunking with all bends, couplers, saddles and expansion joints at not more than 1.0 m fixing centres, UV-resistant grade where external, junction boxes and back-boxes, colour-coded single-core copper line, neutral and protective conductors of 1.5 mm² cross-section, terminations, sealing at every building penetration, circuit identification, and continuity, insulation-resistance and polarity testing on completion. All materials and works shall comply with IEC 60364 and IEC 60227 (latest editions). Measured per linear metre of completed 1.5 mm² circuit. | Supply & Install | m |
| 5.16 | SOL-5.16 | Copper wiring circuit 2.5 mm² — surface conduit / trunking (final circuits) | IEC 60364 / IEC 60227 | Supply and install a final circuit of copper conductors in heavy-duty PVC or steel conduit of not less than 20 mm or trunking fixed on the surface, including the conduit or trunking with all bends, couplers, saddles and expansion joints at not more than 1.0 m fixing centres, UV-resistant grade where external, junction boxes and back-boxes, colour-coded single-core copper line, neutral and protective conductors of 2.5 mm² cross-section, terminations, sealing at every building penetration, circuit identification, and continuity, insulation-resistance and polarity testing on completion. All materials and works shall comply with IEC 60364 and IEC 60227 (latest editions). Measured per linear metre of completed 2.5 mm² circuit. | Supply & Install | m |
| 5.17 | SOL-5.17 | Copper wiring circuit 4 mm² — surface conduit / trunking (final circuits) | IEC 60364 / IEC 60227 | Supply and install a final circuit of copper conductors in heavy-duty PVC or steel conduit of not less than 25 mm or trunking fixed on the surface, including the conduit or trunking with all bends, couplers, saddles and expansion joints at not more than 1.0 m fixing centres, UV-resistant grade where external, junction boxes and back-boxes, colour-coded single-core copper line, neutral and protective conductors of 4 mm² cross-section, terminations, sealing at every building penetration, circuit identification, and continuity, insulation-resistance and polarity testing on completion. All materials and works shall comply with IEC 60364 and IEC 60227 (latest editions). Measured per linear metre of completed 4 mm² circuit. | Supply & Install | m |
| 5.18 | SOL-5.18 | Copper wiring circuit 6 mm² — surface conduit / trunking (final circuits) | IEC 60364 / IEC 60227 | Supply and install a final circuit of copper conductors in heavy-duty PVC or steel conduit of not less than 25 mm or trunking fixed on the surface, including the conduit or trunking with all bends, couplers, saddles and expansion joints at not more than 1.0 m fixing centres, UV-resistant grade where external, junction boxes and back-boxes, colour-coded single-core copper line, neutral and protective conductors of 6 mm² cross-section, terminations, sealing at every building penetration, circuit identification, and continuity, insulation-resistance and polarity testing on completion. All materials and works shall comply with IEC 60364 and IEC 60227 (latest editions). Measured per linear metre of completed 6 mm² circuit. | Supply & Install | m |
| 5.19 | SOL-5.19 | Galvanised perforated cable tray 100 mm wide with covers, supports & earth continuity | IEC 61537 / EN ISO 1461 | Supply and install hot-dip galvanised perforated steel cable tray of 100 mm nominal width, with a side height of not less than 50 mm and a steel thickness of not less than 1.5 mm, complete with covers where exposed to sunlight or falling objects, to carry DC and AC cabling between the array, the inverters, the batteries and the distribution equipment. The works include all bends, tees, risers, reducers and connecting plates of matching manufacture, cantilever arms, channel supports, threaded rod hangers and wall or structure fixings at not more than 1.5 m centres, the segregation of DC, AC and communication cables by physical separation or by internal dividers, earth continuity straps across every joint and the bonding of the tray to the site earthing system, UV-resistant cable ties, the touching-up of all cut edges and damaged galvanising with a zinc-rich coating, fire-stopping at every compartment penetration, and durable route labelling. All materials and works shall comply with IEC 61537 and EN ISO 1461 (latest editions). including a spare capacity of not less than 25%. Measured per linear metre of 100 mm tray installed. | Supply & Install | m |
| 5.20 | SOL-5.20 | Galvanised perforated cable tray 200 mm wide with covers, supports & earth continuity | IEC 61537 / EN ISO 1461 | Supply and install hot-dip galvanised perforated steel cable tray of 200 mm nominal width, with a side height of not less than 50 mm and a steel thickness of not less than 1.5 mm, complete with covers where exposed to sunlight or falling objects, to carry DC and AC cabling between the array, the inverters, the batteries and the distribution equipment. The works include all bends, tees, risers, reducers and connecting plates of matching manufacture, cantilever arms, channel supports, threaded rod hangers and wall or structure fixings at not more than 1.5 m centres, the segregation of DC, AC and communication cables by physical separation or by internal dividers, earth continuity straps across every joint and the bonding of the tray to the site earthing system, UV-resistant cable ties, the touching-up of all cut edges and damaged galvanising with a zinc-rich coating, fire-stopping at every compartment penetration, and durable route labelling. All materials and works shall comply with IEC 61537 and EN ISO 1461 (latest editions). including a spare capacity of not less than 25%. Measured per linear metre of 200 mm tray installed. | Supply & Install | m |
| 5.21 | SOL-5.21 | Galvanised perforated cable tray 300 mm wide with covers, supports & earth continuity | IEC 61537 / EN ISO 1461 | Supply and install hot-dip galvanised perforated steel cable tray of 300 mm nominal width, with a side height of not less than 50 mm and a steel thickness of not less than 1.5 mm, complete with covers where exposed to sunlight or falling objects, to carry DC and AC cabling between the array, the inverters, the batteries and the distribution equipment. The works include all bends, tees, risers, reducers and connecting plates of matching manufacture, cantilever arms, channel supports, threaded rod hangers and wall or structure fixings at not more than 1.5 m centres, the segregation of DC, AC and communication cables by physical separation or by internal dividers, earth continuity straps across every joint and the bonding of the tray to the site earthing system, UV-resistant cable ties, the touching-up of all cut edges and damaged galvanising with a zinc-rich coating, fire-stopping at every compartment penetration, and durable route labelling. All materials and works shall comply with IEC 61537 and EN ISO 1461 (latest editions). including a spare capacity of not less than 25%. Measured per linear metre of 300 mm tray installed. | Supply & Install | m |
| 5.22 | SOL-5.22 | Cable trench 0.60 × 0.40 m — complete: excavate, sand-bed, duct, warning tape, backfill & reinstate | IEC 60364-5-52 | Excavate, form and reinstate a complete cable trench approximately 600 mm deep and 400 mm wide for the burial of DC, AC or control cables between the array, the equipment room and the point of use. The works include the location of existing services before excavation, excavation in any material, the trimming and compaction of the formation, a 100 mm bed of clean sand, the laying of the cable or duct with the specified spacing and without kinks, a further 100 mm of sand surround, protective tiles or a concrete cover slab where required, a continuous polyethylene warning tape 300 mm above the cable, backfilling in compacted layers with approved material, the reinstatement of the surface to match the existing, route marker plates at all changes of direction and at not more than 25 m intervals, and an accurate record of the route on the as-built drawings. All materials and works shall comply with IEC 60364-5-52 (latest editions). Measured per linear metre of completed trench. | Supply & Install | m |
| 5.23 | SOL-5.23 | Power socket outlet 10 A — supply, install & connect | IEC 60884 | Supply, install, connect and test a 10 A power socket outlet, switched and shuttered with an earth contact, of a weatherproof IP55 pattern where external. The works include the back-box, wiring in cable sized for the circuit, conduit or trunking, a protective double-pole circuit breaker in the distribution board, circuit identification, and polarity, earth-continuity and functional testing. All materials and works shall comply with IEC 60884 (latest editions). Measured per socket outlet. | Supply & Install | No. |
| 5.24 | SOL-5.24 | Power socket outlet 16 A — supply, install & connect (dedicated circuit) | IEC 60884 | Supply, install, connect and test a 16 A power socket outlet, single or twin, switched and shuttered with an earth contact, for higher-load appliances such as water heaters, tools and air-conditioning units, of a weatherproof IP55 pattern where external. The works include the back-box, wiring in cable sized for the 16 A circuit, conduit or trunking, a dedicated double-pole protective circuit breaker in the distribution board, durable labelling, and polarity, earth-continuity and functional testing. All materials and works shall comply with IEC 60884 (latest editions). Measured per socket outlet. | Supply & Install | No. |
| 5.25 | SOL-5.25 | Power / lighting switch — 1-way, 2-way or intermediate, single or multi-gang | IEC 60669-1 | Supply, install, connect and test a wall-mounted power or lighting switch of the type stated in the call-off order — one-way, two-way or intermediate, single or multi-gang — rated not less than 10 A 250 V, of a weatherproof IP55 pattern where external and of a moulded flush pattern where internal. The works include the back-box, the switch plate and mechanism, wiring and conduit from the circuit, terminations, durable identification of the circuit or luminaire controlled, and functional testing. All materials and works shall comply with IEC 60669-1 (latest editions). Measured per switch position. | Supply & Install | No. |
| 5.26 | SOL-5.26 | Exhaust / extract fan — general purpose | EN 13141 | Supply, install, wire, test and commission a general-purpose wall or ceiling extract fan serving a toilet, store or plant space within a solar-powered facility, complete with a backdraught shutter, an insect-proof external grille, ducting and a sleeved wall or roof penetration made good and weathertight, a fused spur and local isolator, wiring and conduit from the distribution board, timer or humidistat control where specified, and functional testing on completion. All materials and works shall comply with EN 13141 (latest editions). Measured per fan. | Supply & Install | No. |
| 5.27 | SOL-5.27 | Lighting point — concealed conduit (LED 40 W) | EN 12464-1 / EN 60598 | Supply, install, connect and test a complete interior lighting point served by a solar-powered supply, comprising an LED luminaire of approximately 40 W, wiring in concealed conduit, the back-box, the control switch and the associated socket where shown, all fixings and terminations, circuit identification, and functional and illuminance testing on completion. All materials and works shall comply with EN 12464-1 and EN 60598 (latest editions). Measured per complete point. | Supply & Install | No. |
| 5.28 | SOL-5.28 | Lighting point — surface / external (LED 40 W, IP65) | EN 12464-1 / EN 60598 | Supply, install, connect and test a complete external or surface-mounted lighting point served by a solar-powered supply, comprising an IP65 LED luminaire of approximately 40 W, wiring in surface UV-resistant conduit or trunking, the back-box, the control switch or photocell, all fixings, weatherproof glands and terminations, circuit identification, and functional testing on completion. All materials and works shall comply with EN 12464-1 and EN 60598 (latest editions). Measured per complete point. | Supply & Install | No. |
| 5.29 | SOL-5.29 | Illuminated exit sign (running-man, LED, battery-backed ≥3 h) | ISO 7010 / EN 1838 | Supply, install, connect and test an illuminated LED 'running-man' exit sign with an integral battery giving not less than three hours' autonomy, with the directional legend as required by the escape route. The works include the sign and its fixings or suspension, the permanent live supply and wiring, the commissioning charge, a full-duration discharge test recorded in the commissioning report, and the verification of the viewing distance and mounting height. All materials and works shall comply with ISO 7010 and EN 1838 (latest editions). Measured per sign. | Supply & Install | No. |
| 5.30 | SOL-5.30 | Smoke / heat detector with sounder | EN 14604 / EN 54 | Supply, install, connect and test an interlinked smoke or heat detector with an integral sounder in an inverter or battery room, of the sensing type appropriate to the risk, mains or permanently powered with battery backup. The works include fixing to the soffit at the correct spacing from walls and air movement, interlinking with any adjacent detectors, wiring and conduit, functional testing with approved test aerosol or heat source, labelling, and a demonstration to LRC staff. All materials and works shall comply with EN 14604 and EN 54 (latest editions). Measured per detector. | Supply & Install | No. |
| 5.31 | SOL-5.31 | Power, control & protection devices — circuit breakers, contactors, SPDs, protection & control relays | IEC 60947 / IEC 60898-1 / IEC 61009-1 / IEC 61643-11 / IEC 61439-2 | Supply, transport, install, wire, test and commission the power, control and protection devices for a solar installation, as required by the approved design and the call-off order, to the satisfaction of the LRC Engineer. The item shall be complete including: circuit breakers (MCB / MCCB, double-pole on single-phase circuits) and isolators for the incoming, outgoing and inter-source circuits; contactors and auxiliary relays for source change-over, load shedding and load control; AC surge protective devices with status indicators and backup fuses; protection relays, including an over/under-voltage and phase-failure / phase-sequence relay with adjustable thresholds and automatic time-delayed reconnection on the EDL and generator incoming supplies, and residual-current (earth-leakage) protection where not already provided; control relays, timers and selector switches as required; DIN-rail enclosure or mounting within an existing board, busbars, earth and neutral bars, terminal blocks, glands, ferruled and numbered internal wiring, circuit labelling and a wiring diagram; all manpower, accessories, fittings and fixings; the setting and coordination of all protection devices; and functional, insulation and trip testing with results recorded in the commissioning report. All materials and works shall comply with IEC 60947, IEC 60898-1, IEC 61009-1, IEC 61643-11 and IEC 61439-2 (latest editions). Measured per system, complete and serviceable. | Supply & Install | No. |
|  | SOL-6 SOLAR WATER PUMPING SYSTEMS |  |  |  |  |  |
| 6.1 | SOL-6.01 | Electric panel for solar pumping VFD + sinewave filter (IP54) | IEC 61439-2 / IEC 61800-5-1 | Supply, assemble, install, wire, test and commission a floor-standing or wall-mounted IP54 electric panel to house the solar pumping variable frequency drive and its sinewave output filter. The works include the enclosure with a lockable door, a mounting plate and gland plate, forced or filtered ventilation sized to the drive heat loss, the DC input isolator and fusing from the PV array, the AC output isolator and motor protection, the mains or generator backup input with interlocking where provided, control relays, a level-probe and pressure-switch input terminal block, run, fault and source indication on the front panel, an emergency stop, all internal power, control and CAT6 data cabling with ferruled and numbered terminations, cable glands and supports, an internal earth bar bonded to the site earthing system, a laminated single-line and control diagram inside the door, complete labelling, and functional testing of every circuit. All materials and works shall comply with IEC 61439-2 and IEC 61800-5-1 (latest editions). Measured per panel, complete and serviceable. | Component | No. |
| 6.2 | SOL-6.02 | Solar pumping VFD drive 2 HP | IEC 61800-5-1 / IEC 62109 | Supply, install, configure, test and commission a solar pumping variable frequency drive of 2 HP rating, capable of operating directly from the PV array with integral maximum power point tracking and of switching automatically to a mains or generator supply where available. The works include the drive and its mounting in the panel with the manufacturer's cooling clearances, all required DC and AC power, control and CAT6 data cables, accessories, mounting fittings and protections, input and output filtering and reactors where required by the manufacturer, the configuration of the motor nameplate data, the minimum and maximum frequency, the ramp times, the dry-run and over- and under-voltage protections, the tank-full and tank-empty level inputs and the automatic restart, the setting of the motor thermal-overload protection, cable length compensation, the recording of all parameters in the commissioning report and their handover to LRC on a USB drive, and a demonstration of operation and fault reset to LRC staff. The works also include the supply and installation of the AC power cabling from the VFD to the pump and/or the sinewave filter and/or the control panel, for a total cable route length of up to 50 m, in low-voltage copper cable sized to the drive rating, the permissible voltage drop and the installation method, complete with containment, glands, crimped lugs and terminations (every additional metre beyond 50 m is measured and paid separately under SOL-6.44), together with a complete AC/DC protection panel, fully wired and populated with circuit breakers, fuses with fuse holders, contactors, AC and DC surge protective devices and other protection devices, and all busbars, DIN rails, terminal blocks, earth and neutral bars, cable glands, ferrules, lugs, labels and other accessories needed for a complete and safe installation. All materials and works shall comply with IEC 61800-5-1 and IEC 62109 (latest editions). Measured per unit, complete and serviceable. | Component | No. |
| 6.3 | SOL-6.03 | Solar pumping VFD drive 5 HP | IEC 61800-5-1 / IEC 62109 | Supply, install, configure, test and commission a solar pumping variable frequency drive of 5 HP rating, capable of operating directly from the PV array with integral maximum power point tracking and of switching automatically to a mains or generator supply where available. The works include the drive and its mounting in the panel with the manufacturer's cooling clearances, all required DC and AC power, control and CAT6 data cables, accessories, mounting fittings and protections, input and output filtering and reactors where required by the manufacturer, the configuration of the motor nameplate data, the minimum and maximum frequency, the ramp times, the dry-run and over- and under-voltage protections, the tank-full and tank-empty level inputs and the automatic restart, the setting of the motor thermal-overload protection, cable length compensation, the recording of all parameters in the commissioning report and their handover to LRC on a USB drive, and a demonstration of operation and fault reset to LRC staff. The works also include the supply and installation of the AC power cabling from the VFD to the pump and/or the sinewave filter and/or the control panel, for a total cable route length of up to 50 m, in low-voltage copper cable sized to the drive rating, the permissible voltage drop and the installation method, complete with containment, glands, crimped lugs and terminations (every additional metre beyond 50 m is measured and paid separately under SOL-6.44), together with a complete AC/DC protection panel, fully wired and populated with circuit breakers, fuses with fuse holders, contactors, AC and DC surge protective devices and other protection devices, and all busbars, DIN rails, terminal blocks, earth and neutral bars, cable glands, ferrules, lugs, labels and other accessories needed for a complete and safe installation. All materials and works shall comply with IEC 61800-5-1 and IEC 62109 (latest editions). Measured per unit, complete and serviceable. | Component | No. |
| 6.4 | SOL-6.04 | Solar pumping VFD drive 7.5 HP | IEC 61800-5-1 / IEC 62109 | Supply, install, configure, test and commission a solar pumping variable frequency drive of 7.5 HP rating, capable of operating directly from the PV array with integral maximum power point tracking and of switching automatically to a mains or generator supply where available. The works include the drive and its mounting in the panel with the manufacturer's cooling clearances, all required DC and AC power, control and CAT6 data cables, accessories, mounting fittings and protections, input and output filtering and reactors where required by the manufacturer, the configuration of the motor nameplate data, the minimum and maximum frequency, the ramp times, the dry-run and over- and under-voltage protections, the tank-full and tank-empty level inputs and the automatic restart, the setting of the motor thermal-overload protection, cable length compensation, the recording of all parameters in the commissioning report and their handover to LRC on a USB drive, and a demonstration of operation and fault reset to LRC staff. The works also include the supply and installation of the AC power cabling from the VFD to the pump and/or the sinewave filter and/or the control panel, for a total cable route length of up to 50 m, in low-voltage copper cable sized to the drive rating, the permissible voltage drop and the installation method, complete with containment, glands, crimped lugs and terminations (every additional metre beyond 50 m is measured and paid separately under SOL-6.44), together with a complete AC/DC protection panel, fully wired and populated with circuit breakers, fuses with fuse holders, contactors, AC and DC surge protective devices and other protection devices, and all busbars, DIN rails, terminal blocks, earth and neutral bars, cable glands, ferrules, lugs, labels and other accessories needed for a complete and safe installation. All materials and works shall comply with IEC 61800-5-1 and IEC 62109 (latest editions). Measured per unit, complete and serviceable. | Component | No. |
| 6.5 | SOL-6.05 | Solar pumping VFD drive 10 HP | IEC 61800-5-1 / IEC 62109 | Supply, install, configure, test and commission a solar pumping variable frequency drive of 10 HP rating, capable of operating directly from the PV array with integral maximum power point tracking and of switching automatically to a mains or generator supply where available. The works include the drive and its mounting in the panel with the manufacturer's cooling clearances, all required DC and AC power, control and CAT6 data cables, accessories, mounting fittings and protections, input and output filtering and reactors where required by the manufacturer, the configuration of the motor nameplate data, the minimum and maximum frequency, the ramp times, the dry-run and over- and under-voltage protections, the tank-full and tank-empty level inputs and the automatic restart, the setting of the motor thermal-overload protection, cable length compensation, the recording of all parameters in the commissioning report and their handover to LRC on a USB drive, and a demonstration of operation and fault reset to LRC staff. The works also include the supply and installation of the AC power cabling from the VFD to the pump and/or the sinewave filter and/or the control panel, for a total cable route length of up to 50 m, in low-voltage copper cable sized to the drive rating, the permissible voltage drop and the installation method, complete with containment, glands, crimped lugs and terminations (every additional metre beyond 50 m is measured and paid separately under SOL-6.44), together with a complete AC/DC protection panel, fully wired and populated with circuit breakers, fuses with fuse holders, contactors, AC and DC surge protective devices and other protection devices, and all busbars, DIN rails, terminal blocks, earth and neutral bars, cable glands, ferrules, lugs, labels and other accessories needed for a complete and safe installation. All materials and works shall comply with IEC 61800-5-1 and IEC 62109 (latest editions). Measured per unit, complete and serviceable. | Component | No. |
| 6.6 | SOL-6.06 | Solar pumping VFD drive 15 HP | IEC 61800-5-1 / IEC 62109 | Supply, install, configure, test and commission a solar pumping variable frequency drive of 15 HP rating, capable of operating directly from the PV array with integral maximum power point tracking and of switching automatically to a mains or generator supply where available. The works include the drive and its mounting in the panel with the manufacturer's cooling clearances, all required DC and AC power, control and CAT6 data cables, accessories, mounting fittings and protections, input and output filtering and reactors where required by the manufacturer, the configuration of the motor nameplate data, the minimum and maximum frequency, the ramp times, the dry-run and over- and under-voltage protections, the tank-full and tank-empty level inputs and the automatic restart, the setting of the motor thermal-overload protection, cable length compensation, the recording of all parameters in the commissioning report and their handover to LRC on a USB drive, and a demonstration of operation and fault reset to LRC staff. The works also include the supply and installation of the AC power cabling from the VFD to the pump and/or the sinewave filter and/or the control panel, for a total cable route length of up to 50 m, in low-voltage copper cable sized to the drive rating, the permissible voltage drop and the installation method, complete with containment, glands, crimped lugs and terminations (every additional metre beyond 50 m is measured and paid separately under SOL-6.44), together with a complete AC/DC protection panel, fully wired and populated with circuit breakers, fuses with fuse holders, contactors, AC and DC surge protective devices and other protection devices, and all busbars, DIN rails, terminal blocks, earth and neutral bars, cable glands, ferrules, lugs, labels and other accessories needed for a complete and safe installation. All materials and works shall comply with IEC 61800-5-1 and IEC 62109 (latest editions). Measured per unit, complete and serviceable. | Component | No. |
| 6.7 | SOL-6.07 | Solar pumping VFD drive 20 HP | IEC 61800-5-1 / IEC 62109 | Supply, install, configure, test and commission a solar pumping variable frequency drive of 20 HP rating, capable of operating directly from the PV array with integral maximum power point tracking and of switching automatically to a mains or generator supply where available. The works include the drive and its mounting in the panel with the manufacturer's cooling clearances, all required DC and AC power, control and CAT6 data cables, accessories, mounting fittings and protections, input and output filtering and reactors where required by the manufacturer, the configuration of the motor nameplate data, the minimum and maximum frequency, the ramp times, the dry-run and over- and under-voltage protections, the tank-full and tank-empty level inputs and the automatic restart, the setting of the motor thermal-overload protection, cable length compensation, the recording of all parameters in the commissioning report and their handover to LRC on a USB drive, and a demonstration of operation and fault reset to LRC staff. The works also include the supply and installation of the AC power cabling from the VFD to the pump and/or the sinewave filter and/or the control panel, for a total cable route length of up to 50 m, in low-voltage copper cable sized to the drive rating, the permissible voltage drop and the installation method, complete with containment, glands, crimped lugs and terminations (every additional metre beyond 50 m is measured and paid separately under SOL-6.44), together with a complete AC/DC protection panel, fully wired and populated with circuit breakers, fuses with fuse holders, contactors, AC and DC surge protective devices and other protection devices, and all busbars, DIN rails, terminal blocks, earth and neutral bars, cable glands, ferrules, lugs, labels and other accessories needed for a complete and safe installation. All materials and works shall comply with IEC 61800-5-1 and IEC 62109 (latest editions). Measured per unit, complete and serviceable. | Component | No. |
| 6.8 | SOL-6.08 | Solar pumping VFD drive 25 HP | IEC 61800-5-1 / IEC 62109 | Supply, install, configure, test and commission a solar pumping variable frequency drive of 25 HP rating, capable of operating directly from the PV array with integral maximum power point tracking and of switching automatically to a mains or generator supply where available. The works include the drive and its mounting in the panel with the manufacturer's cooling clearances, all required DC and AC power, control and CAT6 data cables, accessories, mounting fittings and protections, input and output filtering and reactors where required by the manufacturer, the configuration of the motor nameplate data, the minimum and maximum frequency, the ramp times, the dry-run and over- and under-voltage protections, the tank-full and tank-empty level inputs and the automatic restart, the setting of the motor thermal-overload protection, cable length compensation, the recording of all parameters in the commissioning report and their handover to LRC on a USB drive, and a demonstration of operation and fault reset to LRC staff. The works also include the supply and installation of the AC power cabling from the VFD to the pump and/or the sinewave filter and/or the control panel, for a total cable route length of up to 50 m, in low-voltage copper cable sized to the drive rating, the permissible voltage drop and the installation method, complete with containment, glands, crimped lugs and terminations (every additional metre beyond 50 m is measured and paid separately under SOL-6.44), together with a complete AC/DC protection panel, fully wired and populated with circuit breakers, fuses with fuse holders, contactors, AC and DC surge protective devices and other protection devices, and all busbars, DIN rails, terminal blocks, earth and neutral bars, cable glands, ferrules, lugs, labels and other accessories needed for a complete and safe installation. All materials and works shall comply with IEC 61800-5-1 and IEC 62109 (latest editions). Measured per unit, complete and serviceable. | Component | No. |
| 6.9 | SOL-6.09 | Solar pumping VFD drive 30 HP | IEC 61800-5-1 / IEC 62109 | Supply, install, configure, test and commission a solar pumping variable frequency drive of 30 HP rating, capable of operating directly from the PV array with integral maximum power point tracking and of switching automatically to a mains or generator supply where available. The works include the drive and its mounting in the panel with the manufacturer's cooling clearances, all required DC and AC power, control and CAT6 data cables, accessories, mounting fittings and protections, input and output filtering and reactors where required by the manufacturer, the configuration of the motor nameplate data, the minimum and maximum frequency, the ramp times, the dry-run and over- and under-voltage protections, the tank-full and tank-empty level inputs and the automatic restart, the setting of the motor thermal-overload protection, cable length compensation, the recording of all parameters in the commissioning report and their handover to LRC on a USB drive, and a demonstration of operation and fault reset to LRC staff. The works also include the supply and installation of the AC power cabling from the VFD to the pump and/or the sinewave filter and/or the control panel, for a total cable route length of up to 50 m, in low-voltage copper cable sized to the drive rating, the permissible voltage drop and the installation method, complete with containment, glands, crimped lugs and terminations (every additional metre beyond 50 m is measured and paid separately under SOL-6.44), together with a complete AC/DC protection panel, fully wired and populated with circuit breakers, fuses with fuse holders, contactors, AC and DC surge protective devices and other protection devices, and all busbars, DIN rails, terminal blocks, earth and neutral bars, cable glands, ferrules, lugs, labels and other accessories needed for a complete and safe installation. All materials and works shall comply with IEC 61800-5-1 and IEC 62109 (latest editions). Measured per unit, complete and serviceable. | Component | No. |
| 6.10 | SOL-6.10 | Solar pumping VFD drive 40 HP | IEC 61800-5-1 / IEC 62109 | Supply, install, configure, test and commission a solar pumping variable frequency drive of 40 HP rating, capable of operating directly from the PV array with integral maximum power point tracking and of switching automatically to a mains or generator supply where available. The works include the drive and its mounting in the panel with the manufacturer's cooling clearances, all required DC and AC power, control and CAT6 data cables, accessories, mounting fittings and protections, input and output filtering and reactors where required by the manufacturer, the configuration of the motor nameplate data, the minimum and maximum frequency, the ramp times, the dry-run and over- and under-voltage protections, the tank-full and tank-empty level inputs and the automatic restart, the setting of the motor thermal-overload protection, cable length compensation, the recording of all parameters in the commissioning report and their handover to LRC on a USB drive, and a demonstration of operation and fault reset to LRC staff. The works also include the supply and installation of the AC power cabling from the VFD to the pump and/or the sinewave filter and/or the control panel, for a total cable route length of up to 50 m, in low-voltage copper cable sized to the drive rating, the permissible voltage drop and the installation method, complete with containment, glands, crimped lugs and terminations (every additional metre beyond 50 m is measured and paid separately under SOL-6.44), together with a complete AC/DC protection panel, fully wired and populated with circuit breakers, fuses with fuse holders, contactors, AC and DC surge protective devices and other protection devices, and all busbars, DIN rails, terminal blocks, earth and neutral bars, cable glands, ferrules, lugs, labels and other accessories needed for a complete and safe installation. All materials and works shall comply with IEC 61800-5-1 and IEC 62109 (latest editions). Measured per unit, complete and serviceable. | Component | No. |
| 6.11 | SOL-6.11 | Solar pumping VFD drive 50 HP | IEC 61800-5-1 / IEC 62109 | Supply, install, configure, test and commission a solar pumping variable frequency drive of 50 HP rating, capable of operating directly from the PV array with integral maximum power point tracking and of switching automatically to a mains or generator supply where available. The works include the drive and its mounting in the panel with the manufacturer's cooling clearances, all required DC and AC power, control and CAT6 data cables, accessories, mounting fittings and protections, input and output filtering and reactors where required by the manufacturer, the configuration of the motor nameplate data, the minimum and maximum frequency, the ramp times, the dry-run and over- and under-voltage protections, the tank-full and tank-empty level inputs and the automatic restart, the setting of the motor thermal-overload protection, cable length compensation, the recording of all parameters in the commissioning report and their handover to LRC on a USB drive, and a demonstration of operation and fault reset to LRC staff. The works also include the supply and installation of the AC power cabling from the VFD to the pump and/or the sinewave filter and/or the control panel, for a total cable route length of up to 50 m, in low-voltage copper cable sized to the drive rating, the permissible voltage drop and the installation method, complete with containment, glands, crimped lugs and terminations (every additional metre beyond 50 m is measured and paid separately under SOL-6.44), together with a complete AC/DC protection panel, fully wired and populated with circuit breakers, fuses with fuse holders, contactors, AC and DC surge protective devices and other protection devices, and all busbars, DIN rails, terminal blocks, earth and neutral bars, cable glands, ferrules, lugs, labels and other accessories needed for a complete and safe installation. All materials and works shall comply with IEC 61800-5-1 and IEC 62109 (latest editions). Measured per unit, complete and serviceable. | Component | No. |
| 6.12 | SOL-6.12 | Solar pumping VFD drive 60 HP | IEC 61800-5-1 / IEC 62109 | Supply, install, configure, test and commission a solar pumping variable frequency drive of 60 HP rating, capable of operating directly from the PV array with integral maximum power point tracking and of switching automatically to a mains or generator supply where available. The works include the drive and its mounting in the panel with the manufacturer's cooling clearances, all required DC and AC power, control and CAT6 data cables, accessories, mounting fittings and protections, input and output filtering and reactors where required by the manufacturer, the configuration of the motor nameplate data, the minimum and maximum frequency, the ramp times, the dry-run and over- and under-voltage protections, the tank-full and tank-empty level inputs and the automatic restart, the setting of the motor thermal-overload protection, cable length compensation, the recording of all parameters in the commissioning report and their handover to LRC on a USB drive, and a demonstration of operation and fault reset to LRC staff. The works also include the supply and installation of the AC power cabling from the VFD to the pump and/or the sinewave filter and/or the control panel, for a total cable route length of up to 50 m, in low-voltage copper cable sized to the drive rating, the permissible voltage drop and the installation method, complete with containment, glands, crimped lugs and terminations (every additional metre beyond 50 m is measured and paid separately under SOL-6.44), together with a complete AC/DC protection panel, fully wired and populated with circuit breakers, fuses with fuse holders, contactors, AC and DC surge protective devices and other protection devices, and all busbars, DIN rails, terminal blocks, earth and neutral bars, cable glands, ferrules, lugs, labels and other accessories needed for a complete and safe installation. All materials and works shall comply with IEC 61800-5-1 and IEC 62109 (latest editions). Measured per unit, complete and serviceable. | Component | No. |
| 6.13 | SOL-6.13 | Solar pumping VFD drive 70 HP | IEC 61800-5-1 / IEC 62109 | Supply, install, configure, test and commission a solar pumping variable frequency drive of 70 HP rating, capable of operating directly from the PV array with integral maximum power point tracking and of switching automatically to a mains or generator supply where available. The works include the drive and its mounting in the panel with the manufacturer's cooling clearances, all required DC and AC power, control and CAT6 data cables, accessories, mounting fittings and protections, input and output filtering and reactors where required by the manufacturer, the configuration of the motor nameplate data, the minimum and maximum frequency, the ramp times, the dry-run and over- and under-voltage protections, the tank-full and tank-empty level inputs and the automatic restart, the setting of the motor thermal-overload protection, cable length compensation, the recording of all parameters in the commissioning report and their handover to LRC on a USB drive, and a demonstration of operation and fault reset to LRC staff. The works also include the supply and installation of the AC power cabling from the VFD to the pump and/or the sinewave filter and/or the control panel, for a total cable route length of up to 50 m, in low-voltage copper cable sized to the drive rating, the permissible voltage drop and the installation method, complete with containment, glands, crimped lugs and terminations (every additional metre beyond 50 m is measured and paid separately under SOL-6.44), together with a complete AC/DC protection panel, fully wired and populated with circuit breakers, fuses with fuse holders, contactors, AC and DC surge protective devices and other protection devices, and all busbars, DIN rails, terminal blocks, earth and neutral bars, cable glands, ferrules, lugs, labels and other accessories needed for a complete and safe installation. All materials and works shall comply with IEC 61800-5-1 and IEC 62109 (latest editions). Measured per unit, complete and serviceable. | Component | No. |
| 6.14 | SOL-6.14 | Solar pumping VFD drive 80 HP | IEC 61800-5-1 / IEC 62109 | Supply, install, configure, test and commission a solar pumping variable frequency drive of 80 HP rating, capable of operating directly from the PV array with integral maximum power point tracking and of switching automatically to a mains or generator supply where available. The works include the drive and its mounting in the panel with the manufacturer's cooling clearances, all required DC and AC power, control and CAT6 data cables, accessories, mounting fittings and protections, input and output filtering and reactors where required by the manufacturer, the configuration of the motor nameplate data, the minimum and maximum frequency, the ramp times, the dry-run and over- and under-voltage protections, the tank-full and tank-empty level inputs and the automatic restart, the setting of the motor thermal-overload protection, cable length compensation, the recording of all parameters in the commissioning report and their handover to LRC on a USB drive, and a demonstration of operation and fault reset to LRC staff. The works also include the supply and installation of the AC power cabling from the VFD to the pump and/or the sinewave filter and/or the control panel, for a total cable route length of up to 50 m, in low-voltage copper cable sized to the drive rating, the permissible voltage drop and the installation method, complete with containment, glands, crimped lugs and terminations (every additional metre beyond 50 m is measured and paid separately under SOL-6.44), together with a complete AC/DC protection panel, fully wired and populated with circuit breakers, fuses with fuse holders, contactors, AC and DC surge protective devices and other protection devices, and all busbars, DIN rails, terminal blocks, earth and neutral bars, cable glands, ferrules, lugs, labels and other accessories needed for a complete and safe installation. All materials and works shall comply with IEC 61800-5-1 and IEC 62109 (latest editions). Measured per unit, complete and serviceable. | Component | No. |
| 6.15 | SOL-6.15 | Solar pumping VFD drive 90 HP | IEC 61800-5-1 / IEC 62109 | Supply, install, configure, test and commission a solar pumping variable frequency drive of 90 HP rating, capable of operating directly from the PV array with integral maximum power point tracking and of switching automatically to a mains or generator supply where available. The works include the drive and its mounting in the panel with the manufacturer's cooling clearances, all required DC and AC power, control and CAT6 data cables, accessories, mounting fittings and protections, input and output filtering and reactors where required by the manufacturer, the configuration of the motor nameplate data, the minimum and maximum frequency, the ramp times, the dry-run and over- and under-voltage protections, the tank-full and tank-empty level inputs and the automatic restart, the setting of the motor thermal-overload protection, cable length compensation, the recording of all parameters in the commissioning report and their handover to LRC on a USB drive, and a demonstration of operation and fault reset to LRC staff. The works also include the supply and installation of the AC power cabling from the VFD to the pump and/or the sinewave filter and/or the control panel, for a total cable route length of up to 50 m, in low-voltage copper cable sized to the drive rating, the permissible voltage drop and the installation method, complete with containment, glands, crimped lugs and terminations (every additional metre beyond 50 m is measured and paid separately under SOL-6.44), together with a complete AC/DC protection panel, fully wired and populated with circuit breakers, fuses with fuse holders, contactors, AC and DC surge protective devices and other protection devices, and all busbars, DIN rails, terminal blocks, earth and neutral bars, cable glands, ferrules, lugs, labels and other accessories needed for a complete and safe installation. All materials and works shall comply with IEC 61800-5-1 and IEC 62109 (latest editions). Measured per unit, complete and serviceable. | Component | No. |
| 6.16 | SOL-6.16 | Solar pumping VFD drive 100 HP | IEC 61800-5-1 / IEC 62109 | Supply, install, configure, test and commission a solar pumping variable frequency drive of 100 HP rating, capable of operating directly from the PV array with integral maximum power point tracking and of switching automatically to a mains or generator supply where available. The works include the drive and its mounting in the panel with the manufacturer's cooling clearances, all required DC and AC power, control and CAT6 data cables, accessories, mounting fittings and protections, input and output filtering and reactors where required by the manufacturer, the configuration of the motor nameplate data, the minimum and maximum frequency, the ramp times, the dry-run and over- and under-voltage protections, the tank-full and tank-empty level inputs and the automatic restart, the setting of the motor thermal-overload protection, cable length compensation, the recording of all parameters in the commissioning report and their handover to LRC on a USB drive, and a demonstration of operation and fault reset to LRC staff. The works also include the supply and installation of the AC power cabling from the VFD to the pump and/or the sinewave filter and/or the control panel, for a total cable route length of up to 50 m, in low-voltage copper cable sized to the drive rating, the permissible voltage drop and the installation method, complete with containment, glands, crimped lugs and terminations (every additional metre beyond 50 m is measured and paid separately under SOL-6.44), together with a complete AC/DC protection panel, fully wired and populated with circuit breakers, fuses with fuse holders, contactors, AC and DC surge protective devices and other protection devices, and all busbars, DIN rails, terminal blocks, earth and neutral bars, cable glands, ferrules, lugs, labels and other accessories needed for a complete and safe installation. All materials and works shall comply with IEC 61800-5-1 and IEC 62109 (latest editions). Measured per unit, complete and serviceable. | Component | No. |
| 6.17 | SOL-6.17 | Solar pumping VFD drive 125 HP | IEC 61800-5-1 / IEC 62109 | Supply, install, configure, test and commission a solar pumping variable frequency drive of 125 HP rating, capable of operating directly from the PV array with integral maximum power point tracking and of switching automatically to a mains or generator supply where available. The works include the drive and its mounting in the panel with the manufacturer's cooling clearances, all required DC and AC power, control and CAT6 data cables, accessories, mounting fittings and protections, input and output filtering and reactors where required by the manufacturer, the configuration of the motor nameplate data, the minimum and maximum frequency, the ramp times, the dry-run and over- and under-voltage protections, the tank-full and tank-empty level inputs and the automatic restart, the setting of the motor thermal-overload protection, cable length compensation, the recording of all parameters in the commissioning report and their handover to LRC on a USB drive, and a demonstration of operation and fault reset to LRC staff. The works also include the supply and installation of the AC power cabling from the VFD to the pump and/or the sinewave filter and/or the control panel, for a total cable route length of up to 50 m, in low-voltage copper cable sized to the drive rating, the permissible voltage drop and the installation method, complete with containment, glands, crimped lugs and terminations (every additional metre beyond 50 m is measured and paid separately under SOL-6.44), together with a complete AC/DC protection panel, fully wired and populated with circuit breakers, fuses with fuse holders, contactors, AC and DC surge protective devices and other protection devices, and all busbars, DIN rails, terminal blocks, earth and neutral bars, cable glands, ferrules, lugs, labels and other accessories needed for a complete and safe installation. All materials and works shall comply with IEC 61800-5-1 and IEC 62109 (latest editions). Measured per unit, complete and serviceable. | Component | No. |
| 6.18 | SOL-6.18 | Solar pumping VFD drive 150 HP | IEC 61800-5-1 / IEC 62109 | Supply, install, configure, test and commission a solar pumping variable frequency drive of 150 HP rating, capable of operating directly from the PV array with integral maximum power point tracking and of switching automatically to a mains or generator supply where available. The works include the drive and its mounting in the panel with the manufacturer's cooling clearances, all required DC and AC power, control and CAT6 data cables, accessories, mounting fittings and protections, input and output filtering and reactors where required by the manufacturer, the configuration of the motor nameplate data, the minimum and maximum frequency, the ramp times, the dry-run and over- and under-voltage protections, the tank-full and tank-empty level inputs and the automatic restart, the setting of the motor thermal-overload protection, cable length compensation, the recording of all parameters in the commissioning report and their handover to LRC on a USB drive, and a demonstration of operation and fault reset to LRC staff. The works also include the supply and installation of the AC power cabling from the VFD to the pump and/or the sinewave filter and/or the control panel, for a total cable route length of up to 50 m, in low-voltage copper cable sized to the drive rating, the permissible voltage drop and the installation method, complete with containment, glands, crimped lugs and terminations (every additional metre beyond 50 m is measured and paid separately under SOL-6.44), together with a complete AC/DC protection panel, fully wired and populated with circuit breakers, fuses with fuse holders, contactors, AC and DC surge protective devices and other protection devices, and all busbars, DIN rails, terminal blocks, earth and neutral bars, cable glands, ferrules, lugs, labels and other accessories needed for a complete and safe installation. All materials and works shall comply with IEC 61800-5-1 and IEC 62109 (latest editions). Measured per unit, complete and serviceable. | Component | No. |
| 6.19 | SOL-6.19 | Solar pumping VFD drive 180 HP | IEC 61800-5-1 / IEC 62109 | Supply, install, configure, test and commission a solar pumping variable frequency drive of 180 HP rating, capable of operating directly from the PV array with integral maximum power point tracking and of switching automatically to a mains or generator supply where available. The works include the drive and its mounting in the panel with the manufacturer's cooling clearances, all required DC and AC power, control and CAT6 data cables, accessories, mounting fittings and protections, input and output filtering and reactors where required by the manufacturer, the configuration of the motor nameplate data, the minimum and maximum frequency, the ramp times, the dry-run and over- and under-voltage protections, the tank-full and tank-empty level inputs and the automatic restart, the setting of the motor thermal-overload protection, cable length compensation, the recording of all parameters in the commissioning report and their handover to LRC on a USB drive, and a demonstration of operation and fault reset to LRC staff. The works also include the supply and installation of the AC power cabling from the VFD to the pump and/or the sinewave filter and/or the control panel, for a total cable route length of up to 50 m, in low-voltage copper cable sized to the drive rating, the permissible voltage drop and the installation method, complete with containment, glands, crimped lugs and terminations (every additional metre beyond 50 m is measured and paid separately under SOL-6.44), together with a complete AC/DC protection panel, fully wired and populated with circuit breakers, fuses with fuse holders, contactors, AC and DC surge protective devices and other protection devices, and all busbars, DIN rails, terminal blocks, earth and neutral bars, cable glands, ferrules, lugs, labels and other accessories needed for a complete and safe installation. All materials and works shall comply with IEC 61800-5-1 and IEC 62109 (latest editions). Measured per unit, complete and serviceable. | Component | No. |
| 6.2 | SOL-6.20 | Solar pumping VFD drive 200 HP | IEC 61800-5-1 / IEC 62109 | Supply, install, configure, test and commission a solar pumping variable frequency drive of 200 HP rating, capable of operating directly from the PV array with integral maximum power point tracking and of switching automatically to a mains or generator supply where available. The works include the drive and its mounting in the panel with the manufacturer's cooling clearances, all required DC and AC power, control and CAT6 data cables, accessories, mounting fittings and protections, input and output filtering and reactors where required by the manufacturer, the configuration of the motor nameplate data, the minimum and maximum frequency, the ramp times, the dry-run and over- and under-voltage protections, the tank-full and tank-empty level inputs and the automatic restart, the setting of the motor thermal-overload protection, cable length compensation, the recording of all parameters in the commissioning report and their handover to LRC on a USB drive, and a demonstration of operation and fault reset to LRC staff. The works also include the supply and installation of the AC power cabling from the VFD to the pump and/or the sinewave filter and/or the control panel, for a total cable route length of up to 50 m, in low-voltage copper cable sized to the drive rating, the permissible voltage drop and the installation method, complete with containment, glands, crimped lugs and terminations (every additional metre beyond 50 m is measured and paid separately under SOL-6.44), together with a complete AC/DC protection panel, fully wired and populated with circuit breakers, fuses with fuse holders, contactors, AC and DC surge protective devices and other protection devices, and all busbars, DIN rails, terminal blocks, earth and neutral bars, cable glands, ferrules, lugs, labels and other accessories needed for a complete and safe installation. All materials and works shall comply with IEC 61800-5-1 and IEC 62109 (latest editions). Measured per unit, complete and serviceable. | Component | No. |
| 6.21 | SOL-6.21 | Solar pumping VFD drive 250 HP | IEC 61800-5-1 / IEC 62109 | Supply, install, configure, test and commission a solar pumping variable frequency drive of 250 HP rating, capable of operating directly from the PV array with integral maximum power point tracking and of switching automatically to a mains or generator supply where available. The works include the drive and its mounting in the panel with the manufacturer's cooling clearances, all required DC and AC power, control and CAT6 data cables, accessories, mounting fittings and protections, input and output filtering and reactors where required by the manufacturer, the configuration of the motor nameplate data, the minimum and maximum frequency, the ramp times, the dry-run and over- and under-voltage protections, the tank-full and tank-empty level inputs and the automatic restart, the setting of the motor thermal-overload protection, cable length compensation, the recording of all parameters in the commissioning report and their handover to LRC on a USB drive, and a demonstration of operation and fault reset to LRC staff. The works also include the supply and installation of the AC power cabling from the VFD to the pump and/or the sinewave filter and/or the control panel, for a total cable route length of up to 50 m, in low-voltage copper cable sized to the drive rating, the permissible voltage drop and the installation method, complete with containment, glands, crimped lugs and terminations (every additional metre beyond 50 m is measured and paid separately under SOL-6.44), together with a complete AC/DC protection panel, fully wired and populated with circuit breakers, fuses with fuse holders, contactors, AC and DC surge protective devices and other protection devices, and all busbars, DIN rails, terminal blocks, earth and neutral bars, cable glands, ferrules, lugs, labels and other accessories needed for a complete and safe installation. All materials and works shall comply with IEC 61800-5-1 and IEC 62109 (latest editions). Measured per unit, complete and serviceable. | Component | No. |
| 6.22 | SOL-6.22 | Solar pumping VFD drive 300 HP | IEC 61800-5-1 / IEC 62109 | Supply, install, configure, test and commission a solar pumping variable frequency drive of 300 HP rating, capable of operating directly from the PV array with integral maximum power point tracking and of switching automatically to a mains or generator supply where available. The works include the drive and its mounting in the panel with the manufacturer's cooling clearances, all required DC and AC power, control and CAT6 data cables, accessories, mounting fittings and protections, input and output filtering and reactors where required by the manufacturer, the configuration of the motor nameplate data, the minimum and maximum frequency, the ramp times, the dry-run and over- and under-voltage protections, the tank-full and tank-empty level inputs and the automatic restart, the setting of the motor thermal-overload protection, cable length compensation, the recording of all parameters in the commissioning report and their handover to LRC on a USB drive, and a demonstration of operation and fault reset to LRC staff. The works also include the supply and installation of the AC power cabling from the VFD to the pump and/or the sinewave filter and/or the control panel, for a total cable route length of up to 50 m, in low-voltage copper cable sized to the drive rating, the permissible voltage drop and the installation method, complete with containment, glands, crimped lugs and terminations (every additional metre beyond 50 m is measured and paid separately under SOL-6.44), together with a complete AC/DC protection panel, fully wired and populated with circuit breakers, fuses with fuse holders, contactors, AC and DC surge protective devices and other protection devices, and all busbars, DIN rails, terminal blocks, earth and neutral bars, cable glands, ferrules, lugs, labels and other accessories needed for a complete and safe installation. All materials and works shall comply with IEC 61800-5-1 and IEC 62109 (latest editions). Measured per unit, complete and serviceable. | Component | No. |
| 6.23 | SOL-6.23 | Sinewave output filter — for VFD 2 HP | IEC 61800-3 | Supply, install, connect, test and commission a sinewave output filter matched to a 2 HP solar pumping variable frequency drive, to convert the drive's pulse-width-modulated output to a near-sinusoidal waveform so that the submersible motor and its long cable run are protected from voltage reflection, bearing currents and insulation stress. The works include the filter and its mounting with the manufacturer's cooling clearances, all required power, control and earthing cables, accessories, mounting fittings and protections, the setting of the drive switching frequency to the filter manufacturer's requirement, thermal protection where provided, and the verification of the output waveform and motor terminal voltage on commissioning. All materials and works shall comply with IEC 61800-3 (latest editions). Measured per unit, complete and serviceable. | Component | No. |
| 6.24 | SOL-6.24 | Sinewave output filter — for VFD 5 HP | IEC 61800-3 | Supply, install, connect, test and commission a sinewave output filter matched to a 5 HP solar pumping variable frequency drive, to convert the drive's pulse-width-modulated output to a near-sinusoidal waveform so that the submersible motor and its long cable run are protected from voltage reflection, bearing currents and insulation stress. The works include the filter and its mounting with the manufacturer's cooling clearances, all required power, control and earthing cables, accessories, mounting fittings and protections, the setting of the drive switching frequency to the filter manufacturer's requirement, thermal protection where provided, and the verification of the output waveform and motor terminal voltage on commissioning. All materials and works shall comply with IEC 61800-3 (latest editions). Measured per unit, complete and serviceable. | Component | No. |
| 6.25 | SOL-6.25 | Sinewave output filter — for VFD 7.5 HP | IEC 61800-3 | Supply, install, connect, test and commission a sinewave output filter matched to a 7.5 HP solar pumping variable frequency drive, to convert the drive's pulse-width-modulated output to a near-sinusoidal waveform so that the submersible motor and its long cable run are protected from voltage reflection, bearing currents and insulation stress. The works include the filter and its mounting with the manufacturer's cooling clearances, all required power, control and earthing cables, accessories, mounting fittings and protections, the setting of the drive switching frequency to the filter manufacturer's requirement, thermal protection where provided, and the verification of the output waveform and motor terminal voltage on commissioning. All materials and works shall comply with IEC 61800-3 (latest editions). Measured per unit, complete and serviceable. | Component | No. |
| 6.26 | SOL-6.26 | Sinewave output filter — for VFD 10 HP | IEC 61800-3 | Supply, install, connect, test and commission a sinewave output filter matched to a 10 HP solar pumping variable frequency drive, to convert the drive's pulse-width-modulated output to a near-sinusoidal waveform so that the submersible motor and its long cable run are protected from voltage reflection, bearing currents and insulation stress. The works include the filter and its mounting with the manufacturer's cooling clearances, all required power, control and earthing cables, accessories, mounting fittings and protections, the setting of the drive switching frequency to the filter manufacturer's requirement, thermal protection where provided, and the verification of the output waveform and motor terminal voltage on commissioning. All materials and works shall comply with IEC 61800-3 (latest editions). Measured per unit, complete and serviceable. | Component | No. |
| 6.27 | SOL-6.27 | Sinewave output filter — for VFD 15 HP | IEC 61800-3 | Supply, install, connect, test and commission a sinewave output filter matched to a 15 HP solar pumping variable frequency drive, to convert the drive's pulse-width-modulated output to a near-sinusoidal waveform so that the submersible motor and its long cable run are protected from voltage reflection, bearing currents and insulation stress. The works include the filter and its mounting with the manufacturer's cooling clearances, all required power, control and earthing cables, accessories, mounting fittings and protections, the setting of the drive switching frequency to the filter manufacturer's requirement, thermal protection where provided, and the verification of the output waveform and motor terminal voltage on commissioning. All materials and works shall comply with IEC 61800-3 (latest editions). Measured per unit, complete and serviceable. | Component | No. |
| 6.28 | SOL-6.28 | Sinewave output filter — for VFD 20 HP | IEC 61800-3 | Supply, install, connect, test and commission a sinewave output filter matched to a 20 HP solar pumping variable frequency drive, to convert the drive's pulse-width-modulated output to a near-sinusoidal waveform so that the submersible motor and its long cable run are protected from voltage reflection, bearing currents and insulation stress. The works include the filter and its mounting with the manufacturer's cooling clearances, all required power, control and earthing cables, accessories, mounting fittings and protections, the setting of the drive switching frequency to the filter manufacturer's requirement, thermal protection where provided, and the verification of the output waveform and motor terminal voltage on commissioning. All materials and works shall comply with IEC 61800-3 (latest editions). Measured per unit, complete and serviceable. | Component | No. |
| 6.29 | SOL-6.29 | Sinewave output filter — for VFD 25 HP | IEC 61800-3 | Supply, install, connect, test and commission a sinewave output filter matched to a 25 HP solar pumping variable frequency drive, to convert the drive's pulse-width-modulated output to a near-sinusoidal waveform so that the submersible motor and its long cable run are protected from voltage reflection, bearing currents and insulation stress. The works include the filter and its mounting with the manufacturer's cooling clearances, all required power, control and earthing cables, accessories, mounting fittings and protections, the setting of the drive switching frequency to the filter manufacturer's requirement, thermal protection where provided, and the verification of the output waveform and motor terminal voltage on commissioning. All materials and works shall comply with IEC 61800-3 (latest editions). Measured per unit, complete and serviceable. | Component | No. |
| 6.3 | SOL-6.30 | Sinewave output filter — for VFD 30 HP | IEC 61800-3 | Supply, install, connect, test and commission a sinewave output filter matched to a 30 HP solar pumping variable frequency drive, to convert the drive's pulse-width-modulated output to a near-sinusoidal waveform so that the submersible motor and its long cable run are protected from voltage reflection, bearing currents and insulation stress. The works include the filter and its mounting with the manufacturer's cooling clearances, all required power, control and earthing cables, accessories, mounting fittings and protections, the setting of the drive switching frequency to the filter manufacturer's requirement, thermal protection where provided, and the verification of the output waveform and motor terminal voltage on commissioning. All materials and works shall comply with IEC 61800-3 (latest editions). Measured per unit, complete and serviceable. | Component | No. |
| 6.31 | SOL-6.31 | Sinewave output filter — for VFD 40 HP | IEC 61800-3 | Supply, install, connect, test and commission a sinewave output filter matched to a 40 HP solar pumping variable frequency drive, to convert the drive's pulse-width-modulated output to a near-sinusoidal waveform so that the submersible motor and its long cable run are protected from voltage reflection, bearing currents and insulation stress. The works include the filter and its mounting with the manufacturer's cooling clearances, all required power, control and earthing cables, accessories, mounting fittings and protections, the setting of the drive switching frequency to the filter manufacturer's requirement, thermal protection where provided, and the verification of the output waveform and motor terminal voltage on commissioning. All materials and works shall comply with IEC 61800-3 (latest editions). Measured per unit, complete and serviceable. | Component | No. |
| 6.32 | SOL-6.32 | Sinewave output filter — for VFD 50 HP | IEC 61800-3 | Supply, install, connect, test and commission a sinewave output filter matched to a 50 HP solar pumping variable frequency drive, to convert the drive's pulse-width-modulated output to a near-sinusoidal waveform so that the submersible motor and its long cable run are protected from voltage reflection, bearing currents and insulation stress. The works include the filter and its mounting with the manufacturer's cooling clearances, all required power, control and earthing cables, accessories, mounting fittings and protections, the setting of the drive switching frequency to the filter manufacturer's requirement, thermal protection where provided, and the verification of the output waveform and motor terminal voltage on commissioning. All materials and works shall comply with IEC 61800-3 (latest editions). Measured per unit, complete and serviceable. | Component | No. |
| 6.33 | SOL-6.33 | Sinewave output filter — for VFD 60 HP | IEC 61800-3 | Supply, install, connect, test and commission a sinewave output filter matched to a 60 HP solar pumping variable frequency drive, to convert the drive's pulse-width-modulated output to a near-sinusoidal waveform so that the submersible motor and its long cable run are protected from voltage reflection, bearing currents and insulation stress. The works include the filter and its mounting with the manufacturer's cooling clearances, all required power, control and earthing cables, accessories, mounting fittings and protections, the setting of the drive switching frequency to the filter manufacturer's requirement, thermal protection where provided, and the verification of the output waveform and motor terminal voltage on commissioning. All materials and works shall comply with IEC 61800-3 (latest editions). Measured per unit, complete and serviceable. | Component | No. |
| 6.34 | SOL-6.34 | Sinewave output filter — for VFD 70 HP | IEC 61800-3 | Supply, install, connect, test and commission a sinewave output filter matched to a 70 HP solar pumping variable frequency drive, to convert the drive's pulse-width-modulated output to a near-sinusoidal waveform so that the submersible motor and its long cable run are protected from voltage reflection, bearing currents and insulation stress. The works include the filter and its mounting with the manufacturer's cooling clearances, all required power, control and earthing cables, accessories, mounting fittings and protections, the setting of the drive switching frequency to the filter manufacturer's requirement, thermal protection where provided, and the verification of the output waveform and motor terminal voltage on commissioning. All materials and works shall comply with IEC 61800-3 (latest editions). Measured per unit, complete and serviceable. | Component | No. |
| 6.35 | SOL-6.35 | Sinewave output filter — for VFD 80 HP | IEC 61800-3 | Supply, install, connect, test and commission a sinewave output filter matched to an 80 HP solar pumping variable frequency drive, to convert the drive's pulse-width-modulated output to a near-sinusoidal waveform so that the submersible motor and its long cable run are protected from voltage reflection, bearing currents and insulation stress. The works include the filter and its mounting with the manufacturer's cooling clearances, all required power, control and earthing cables, accessories, mounting fittings and protections, the setting of the drive switching frequency to the filter manufacturer's requirement, thermal protection where provided, and the verification of the output waveform and motor terminal voltage on commissioning. All materials and works shall comply with IEC 61800-3 (latest editions). Measured per unit, complete and serviceable. | Component | No. |
| 6.36 | SOL-6.36 | Sinewave output filter — for VFD 90 HP | IEC 61800-3 | Supply, install, connect, test and commission a sinewave output filter matched to a 90 HP solar pumping variable frequency drive, to convert the drive's pulse-width-modulated output to a near-sinusoidal waveform so that the submersible motor and its long cable run are protected from voltage reflection, bearing currents and insulation stress. The works include the filter and its mounting with the manufacturer's cooling clearances, all required power, control and earthing cables, accessories, mounting fittings and protections, the setting of the drive switching frequency to the filter manufacturer's requirement, thermal protection where provided, and the verification of the output waveform and motor terminal voltage on commissioning. All materials and works shall comply with IEC 61800-3 (latest editions). Measured per unit, complete and serviceable. | Component | No. |
| 6.37 | SOL-6.37 | Sinewave output filter — for VFD 100 HP | IEC 61800-3 | Supply, install, connect, test and commission a sinewave output filter matched to a 100 HP solar pumping variable frequency drive, to convert the drive's pulse-width-modulated output to a near-sinusoidal waveform so that the submersible motor and its long cable run are protected from voltage reflection, bearing currents and insulation stress. The works include the filter and its mounting with the manufacturer's cooling clearances, all required power, control and earthing cables, accessories, mounting fittings and protections, the setting of the drive switching frequency to the filter manufacturer's requirement, thermal protection where provided, and the verification of the output waveform and motor terminal voltage on commissioning. All materials and works shall comply with IEC 61800-3 (latest editions). Measured per unit, complete and serviceable. | Component | No. |
| 6.38 | SOL-6.38 | Sinewave output filter — for VFD 125 HP | IEC 61800-3 | Supply, install, connect, test and commission a sinewave output filter matched to a 125 HP solar pumping variable frequency drive, to convert the drive's pulse-width-modulated output to a near-sinusoidal waveform so that the submersible motor and its long cable run are protected from voltage reflection, bearing currents and insulation stress. The works include the filter and its mounting with the manufacturer's cooling clearances, all required power, control and earthing cables, accessories, mounting fittings and protections, the setting of the drive switching frequency to the filter manufacturer's requirement, thermal protection where provided, and the verification of the output waveform and motor terminal voltage on commissioning. All materials and works shall comply with IEC 61800-3 (latest editions). Measured per unit, complete and serviceable. | Component | No. |
| 6.39 | SOL-6.39 | Sinewave output filter — for VFD 150 HP | IEC 61800-3 | Supply, install, connect, test and commission a sinewave output filter matched to a 150 HP solar pumping variable frequency drive, to convert the drive's pulse-width-modulated output to a near-sinusoidal waveform so that the submersible motor and its long cable run are protected from voltage reflection, bearing currents and insulation stress. The works include the filter and its mounting with the manufacturer's cooling clearances, all required power, control and earthing cables, accessories, mounting fittings and protections, the setting of the drive switching frequency to the filter manufacturer's requirement, thermal protection where provided, and the verification of the output waveform and motor terminal voltage on commissioning. All materials and works shall comply with IEC 61800-3 (latest editions). Measured per unit, complete and serviceable. | Component | No. |
| 6.4 | SOL-6.40 | Sinewave output filter — for VFD 180 HP | IEC 61800-3 | Supply, install, connect, test and commission a sinewave output filter matched to a 180 HP solar pumping variable frequency drive, to convert the drive's pulse-width-modulated output to a near-sinusoidal waveform so that the submersible motor and its long cable run are protected from voltage reflection, bearing currents and insulation stress. The works include the filter and its mounting with the manufacturer's cooling clearances, all required power, control and earthing cables, accessories, mounting fittings and protections, the setting of the drive switching frequency to the filter manufacturer's requirement, thermal protection where provided, and the verification of the output waveform and motor terminal voltage on commissioning. All materials and works shall comply with IEC 61800-3 (latest editions). Measured per unit, complete and serviceable. | Component | No. |
| 6.41 | SOL-6.41 | Sinewave output filter — for VFD 200 HP | IEC 61800-3 | Supply, install, connect, test and commission a sinewave output filter matched to a 200 HP solar pumping variable frequency drive, to convert the drive's pulse-width-modulated output to a near-sinusoidal waveform so that the submersible motor and its long cable run are protected from voltage reflection, bearing currents and insulation stress. The works include the filter and its mounting with the manufacturer's cooling clearances, all required power, control and earthing cables, accessories, mounting fittings and protections, the setting of the drive switching frequency to the filter manufacturer's requirement, thermal protection where provided, and the verification of the output waveform and motor terminal voltage on commissioning. All materials and works shall comply with IEC 61800-3 (latest editions). Measured per unit, complete and serviceable. | Component | No. |
| 6.42 | SOL-6.42 | Sinewave output filter — for VFD 250 HP | IEC 61800-3 | Supply, install, connect, test and commission a sinewave output filter matched to a 250 HP solar pumping variable frequency drive, to convert the drive's pulse-width-modulated output to a near-sinusoidal waveform so that the submersible motor and its long cable run are protected from voltage reflection, bearing currents and insulation stress. The works include the filter and its mounting with the manufacturer's cooling clearances, all required power, control and earthing cables, accessories, mounting fittings and protections, the setting of the drive switching frequency to the filter manufacturer's requirement, thermal protection where provided, and the verification of the output waveform and motor terminal voltage on commissioning. All materials and works shall comply with IEC 61800-3 (latest editions). Measured per unit, complete and serviceable. | Component | No. |
| 6.43 | SOL-6.43 | Sinewave output filter — for VFD 300 HP | IEC 61800-3 | Supply, install, connect, test and commission a sinewave output filter matched to a 300 HP solar pumping variable frequency drive, to convert the drive's pulse-width-modulated output to a near-sinusoidal waveform so that the submersible motor and its long cable run are protected from voltage reflection, bearing currents and insulation stress. The works include the filter and its mounting with the manufacturer's cooling clearances, all required power, control and earthing cables, accessories, mounting fittings and protections, the setting of the drive switching frequency to the filter manufacturer's requirement, thermal protection where provided, and the verification of the output waveform and motor terminal voltage on commissioning. All materials and works shall comply with IEC 61800-3 (latest editions). Measured per unit, complete and serviceable. | Component | No. |
| 6.44 | SOL-6.44 | Additional cable run beyond the first 50 m (array to pump / panel) | IEC 60364-5-52 | Supply and install the additional cable run required where the distance between the PV array, the control panel and the pump exceeds 50 metres, the first 50 metres being deemed included in the associated items. The works include cable of the cross-section re-calculated for the extended route so that the voltage drop remains within the design limit, containment in tray, duct or trench as appropriate, all supports, glands and terminations, joint-free runs wherever practicable, route marking, and continuity and insulation testing. All materials and works shall comply with IEC 60364-5-52 (latest editions). Measured per linear metre in excess of the first 50 m. | Component | m |
| 6.45 | SOL-6.45 | Pump control panel with float / pressure switch & tank level control | IEC 61439-2 | Supply, install, wire, test and commission a pump control panel in an IP54 enclosure, providing direct-on-line or soft start, motor overload and phase-failure protection, hand-off-auto selection, run and fault indication, and automatic control from a tank level float or electrode probe and a pressure switch so that the pump stops on tank-full and on low source level. The works include the level probe or float set with its cable and mounting in the tank and the source, the pressure switch and its isolating cock, all power and control wiring with ferruled terminations, glands, earthing and bonding, labelling, a wiring diagram inside the door, the setting and recording of all levels and pressures, and functional testing of every automatic and manual mode. All materials and works shall comply with IEC 61439-2 (latest editions). Measured per panel. | Supply & Install | No. |
| 6.46 | SOL-6.46 | Borehole water level monitoring & dry-run protection — submersible level sensor with sounding pipe | IEC 60529 (IP68) / IEC 61326-1 | Supply, install, connect, calibrate, test and commission a borehole water level monitoring system to protect the submersible pump against dry running and to give LRC a continuous reading of the water level in the well. The system comprises a submersible hydrostatic level transmitter of stainless steel construction, IP68, 4–20 mA output, with a measuring range suited to the borehole depth and drawdown stated in the call-off order, suspended below the lowest expected dynamic water level and above the pump intake on a vented polyurethane cable with a stainless steel suspension wire or clamps; alternatively, where approved by the Engineer, stainless steel electrode probes for low-level cut-out. The works include a uPVC or HDPE sounding (dip) pipe of not less than 25 mm diameter fixed alongside the rising main from the wellhead to below the pump level, with a slotted bottom section and a lockable cap, to allow manual dipper measurement; the cable run and its protection from the wellhead to the control panel; the wellhead cable gland and sealing; the connection of the sensor to the VFD or pump control panel dry-run and low-level inputs, with a local digital display of the water level in metres; the setting of the low-level stop, restart level and time delay; surge protection on the signal line; labelling; the recording of the static and dynamic water levels and of all settings in the commissioning report; and the functional test of the pump stopping on low level and restarting on recovery. All materials and works shall comply with IEC 60529 (IP68) and IEC 61326-1 (latest editions). Measured per borehole, complete and serviceable. | Supply & Install | No. |
|  | SOL-7 ENGINEERING DOCUMENTATION & HANDOVER |  |  |  |  |  |
| 7.1 | SOL-7.01 | Engineering design, calculations & shop drawings for a solar installation (pre-construction) (2 hard copies + soft copy on USB and by email ) | IEC 62548 / IEC 62446-1 / EN 1991 | Prepare, submit and obtain the Engineer's approval of the complete engineering design package for a solar installation before any work commences on site. The submission shall include a measured site survey with a shading analysis over the whole year; the energy demand assessment and the system sizing calculation for the PV array, the inverter and the battery autonomy; the pump and array sizing calculation with the duty point where a pumping system is involved; the electrical single-line diagram showing all protection, isolation and earthing; the cable sizing and voltage-drop calculations for every DC and AC circuit; the protection coordination and surge-protection scheme; the earthing and lightning-protection design with the IEC 62305 risk assessment; the structural calculation and shop drawings for the mounting or elevated structure with the wind loading and the roof or foundation loading check; the layout drawings showing the array, the equipment room, the cable routes and the interfaces with existing services; the equipment schedule with the manufacturer's data sheets and certificates; and the method statement and risk assessment for the works. Two signed and stamped hard copies and one editable soft copy in AutoCAD and PDF format shall be submitted. Priced as a lump sum per system. in TWO hard copies and ONE soft copy on a USB drive and by email All materials and works shall comply with IEC 62548, IEC 62446-1 and EN 1991 (latest editions). | Service | No. |
| 7.2 | SOL-7.02 | As-built drawings of the completed solar installation (AutoCAD + PDF) (2 hard copies + soft copy on USB and by email) | — | Prepare and submit complete as-built drawings recording the solar installation exactly as constructed. The submission shall include the array layout with the module, string and mounting positions; the equipment room layout; the final electrical single-line diagram with all device ratings and settings as installed; the routes, depths and sizes of all buried and surface cables with dimensions from permanent features so that they can be located in future; the earthing and lightning-protection layout with the measured earth resistance; the pumping and pipework layout with the pump setting depth and the riser details where applicable; and the panel schedules and labelling schedule. Drawings shall be issued as two stamped and signed A3 or A1 hard copies and as editable AutoCAD (.dwg) and PDF files, titled and numbered to LRC's convention. Priced as a lump sum per system. in TWO hard copies and ONE soft copy on a USB drive and by email | Service | No. |
| 7.3 | SOL-7.03 | O&M manual (2 hard copies + soft copy on USB and by email) & warranty certificates | — | Prepare, print, bind and hand over the operation and maintenance documentation for the completed solar installation, in TWO hard copies and ONE soft copy on a USB drive and by email, with all narrative text in Arabic and English. The manual shall contain a description of the system and its operating strategy; step-by-step start-up, normal operation, shutdown and emergency shutdown procedures; the fault-finding guide with the meaning of every inverter, drive and BMS alarm code and the action required; the planned preventive maintenance schedule with the frequency of each task including module cleaning, torque checks, terminal inspection, filter and battery checks; the safety instructions for working on DC, battery and high-voltage circuits; the manufacturers' original manuals and data sheets for every item of equipment; the commissioning and test records; the as-built drawings; the spare-parts list with the manufacturers' part numbers and local suppliers; the recorded parameter settings of every inverter and drive; and the ORIGINAL WARRANTY CERTIFICATES for the modules, the inverter, the batteries, the pump and the workmanship, each stating the start date, the duration and the claim procedure. The USB drive shall carry the same content in PDF together with the editable drawings and the parameter files. Measured per set. | Service | Set |
|  | SOL-8 DAYWORKS |  |  |  |  |  |
| 8.1 | SOL-8.01 | Dayworks — solar / electrical technician (per man-day, 8 hours) | — | Provide a skilled solar or electrical technician for instructed work The rate covers one man-day of eight working hours on site including travel, hand tools, personal protective equipment and all associated costs; it excludes materials. Time shall be recorded on a daywork sheet signed daily by the Engineer. Measured per man-day with 0.25 portions | Service | day |